## Generation Thermal Headroom
Version 1.0 | [7 empty] | Generation Thermal Demand Headroom (MVA)
| Please filter on your selected substation | [6 empty] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2035 | 2040 | 2045 | 2050
Licence Area | Substation Name | Voltage (kV) | Supply Voltage (kV) | BSP Group | GSP | Substation Location | Scenario (Short Name) | [14 empty] | Bulk Supply Point or Primary | Scenario Full Name | Output Parameter
NPgN | ANNFIELD | 66 | 132 | Annfield | STELLA SOUTH | DH9 7XW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BARRACK ROAD | 33 | 132 | Barrack Road | STELLA NORTH | NE4 6DB | PS (Best View Plan) | 114.328 | 114.015 | 113.665 | 113.288 | 112.867 | 112.417 | 111.982 | 111.562 | 111.148 | 110.742 | 109.114 | 107.95 | 107.29 | 106.73 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER | 33 | 132 | Blucher | STELLA NORTH | NE15 9SD | PS (Best View Plan) | 94.003 | 93.305 | 92.474 | 91.769 | 91.021 | 90.199 | 89.397 | 88.64 | 87.957 | 87.234 | 84.737 | 82.557 | 81.387 | 80.415 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD | 33 | 132 | Bowesfield | NORTON | TS18 3HP | PS (Best View Plan) | 61.151 | 58.685 | 55.422 | 53.833 | 52.488 | 50.808 | 49.111 | 47.689 | 46.929 | 45.652 | 44.815 | 40.341 | 38.689 | 37.587 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CHIRTON GRANGE | 33 | 132 | Chirton Grange | TYNEMOUTH | NE29 8EY | PS (Best View Plan) | 61.52 | 60.873 | 60.131 | 59.403 | 58.605 | 57.745 | 56.909 | 56.108 | 55.342 | 54.571 | 51.623 | 49.359 | 48.092 | 47.022 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | COALBURNS | 66 | 132 | Coalburns | STELLA SOUTH | NE40 4JP | PS (Best View Plan) | 69.646 | 67.433 | 64.37 | 63.317 | 62.642 | 61.634 | 60.57 | 59.79 | 59.761 | 59.104 | 61.412 | 58.479 | 57.757 | 57.452 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL | 33 | 132 | Darlington Central | NORTON | DL1 1HG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON NORTH | 33 | 132 | Darlington North | NORTON | DL3 0XE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON | 66 | 132 | Dunston | STELLA NORTH | NE11 9DH | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH | 33 | 132 | Flatworth | TYNEMOUTH | NE29 7FN | PS (Best View Plan) | 27.06 | 26.751 | 26.402 | 26.039 | 25.635 | 25.203 | 24.785 | 24.382 | 23.99 | 23.602 | 22.073 | 20.956 | 20.329 | 19.799 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH | 33 | 132 | Gosforth | TYNEMOUTH | NE3 1XL | PS (Best View Plan) | 88.47 | 87.9 | 87.254 | 86.592 | 85.859 | 85.073 | 84.311 | 83.579 | 82.869 | 82.165 | 79.412 | 77.378 | 76.24 | 75.282 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/33KV | 33 | 132 | Harrogate 132/33kV | KNARESBOROUGH | HG1 2LA | PS (Best View Plan) | 45.483 | 44.731 | 43.811 | 43.119 | 42.41 | 41.613 | 40.827 | 40.094 | 39.462 | 38.753 | 36.503 | 34.223 | 32.965 | 31.898 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE | 33 | 132 | Husthwaite | KNARESBOROUGH | YO61 4PN | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | Leeming Bar_Skeeby | NORTON | DL7 0RL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | LINTON | 66 | 132 | Linton | BLYTH 132kV | NE61 5DA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MALTON GRID | 66 | 132 | Malton Grid | OSBALDWICK | YO17 6RD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 132/33kV | 33 | 132 | Melrosegate | OSBALDWICK | YO31 0YB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES | 66 | 132 | North Tees | NORTON | TS23 1PY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE 132/66kV | 66 | 132 | Potter House | SPENNYMOOR | DH1 5FF | PS (Best View Plan) | 88.684 | 87.262 | 85.46 | 84.326 | 83.238 | 81.972 | 80.715 | 79.585 | 78.734 | 77.673 | 75.157 | 71.684 | 70.011 | 68.684 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSWORTH | 66 | 132 | Ravensworth | STELLA SOUTH | DH3 1RQ | PS (Best View Plan) | 76.138 | 75.655 | 75.043 | 74.659 | 74.29 | 73.862 | 73.437 | 73.057 | 72.774 | 72.42 | 71.607 | 70.47 | 69.947 | 69.543 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH GRID | 33 | 132 | Scarborough Grid | OSBALDWICK | YO11 2YH | PS (Best View Plan) | 70.668 | 68.655 | 66.008 | 64.668 | 63.507 | 62.072 | 60.623 | 59.384 | 58.657 | 57.518 | 56.232 | 52.19 | 50.474 | 49.2 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SEAL SANDS | 66 | 132 | Seal Sands | SALTHOLME | TS2 1FB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5LJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO | 66 | 132 | Toronto | SPENNYMOOR | DL14 7RJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 3PS | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ATTERCLIFFE | 33 | 132 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3FA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 132/66KV | 66 | 132 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1LR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6NJ | PS (Best View Plan) | 66.9144 | 65.8474 | 64.3714 | 63.5444 | 62.8564 | 61.9134 | 60.9234 | 60.0404 | 59.4274 | 58.5974 | 56.2344 | 53.6514 | 52.2334 | 51.0174 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BEVERLEY 132/33KV | 33 | 132 | Beverley 132/33kV | CREYKE BECK | HU17 0RW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 132/33KV | 33 | 132 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | PS (Best View Plan) | 9.5386 | 9.0286 | 8.4456 | 7.8526 | 7.2006 | 6.4946 | 5.8066 | 5.1396 | 4.4896 | 3.8376 | 1.2246 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS B | 33 | 132 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1DA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BLYTON | 33 | 132 | Blyton | KEADBY | DN21 3NS | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BRADFORD | 33 | 132 | Bradford | BRADFORD WEST | BD1 4RF | PS (Best View Plan) | 99.226 | 98.599 | 97.897 | 97.141 | 96.299 | 95.398 | 94.524 | 93.673 | 92.829 | 91.995 | 88.598 | 86.116 | 84.631 | 83.337 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHAM | 33 | 132 | Bramham | FERRYBRIDGE B | LS24 9NT | PS (Best View Plan) | 25.4807 | 22.0417 | 16.5717 | 15.0597 | 14.7267 | 13.1697 | 11.2247 | 9.7737 | 9.8197 | 8.5627 | 9.1257 | 4.4647 | 2.1867 | 0.21972 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BRANSHOLME | 33 | 132 | Bransholme | CREYKE BECK | HU7 4ZN | PS (Best View Plan) | 65.2383 | 64.3313 | 63.0553 | 62.3853 | 61.8543 | 61.0953 | 60.2893 | 59.5773 | 59.1123 | 58.4463 | 56.6583 | 54.5543 | 53.4003 | 52.4083 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | Brighouse 132/33kV | ELLAND | HD6 1PZ | PS (Best View Plan) | 95.4417 | 94.3297 | 92.7337 | 91.9647 | 91.4007 | 90.5387 | 89.6057 | 88.7937 | 88.3097 | 87.5487 | 85.6727 | 83.1957 | 81.8147 | 80.6107 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 8UX | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER CENTRAL | 33 | 132 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1RE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | Driffield/Beverley Group | CREYKE BECK | YO25 5NW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FEATHERSTONE | 33 | 132 | Featherstone | FERRYBRIDGE B | WF7 6HE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GIRLINGTON | 33 | 132 | Girlington | BRADFORD WEST | BD7 2NB | PS (Best View Plan) | 84.9795 | 84.6005 | 84.1755 | 83.7185 | 83.2095 | 82.6645 | 82.1355 | 81.6205 | 81.1105 | 80.6065 | 78.5515 | 77.0505 | 76.1525 | 75.3695 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 132/33KV | 33 | 132 | Halifax 132/33kV | ELLAND | HX1 1XB | PS (Best View Plan) | 1.3236 | 1.1186 | 0.88962 | 0.64362 | 0.37062 | 0.077619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HECKMONDWIKE | 33 | 132 | Heckmondwike | SKELTON GRANGE | WF16 9LU | PS (Best View Plan) | 88.487 | 88.046 | 87.552 | 87.021 | 86.429 | 85.796 | 85.181 | 84.581 | 83.984 | 83.394 | 80.978 | 79.203 | 78.125 | 77.18 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HOLMFIELD | 33 | 132 | Holmfield | BRADFORD WEST | HX2 9AY | PS (Best View Plan) | 56.7715 | 56.0885 | 55.3255 | 54.5055 | 53.5925 | 52.6165 | 51.6635 | 50.7295 | 49.7955 | 48.8665 | 45.0235 | 42.1575 | 40.3575 | 38.7545 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 132/33KV | 33 | 132 | Hull East 132/33kV | SALTEND NORTH | HU9 5NL | PS (Best View Plan) | 8.1447 | 7.4707 | 6.7147 | 5.9127 | 5.0307 | 4.0787 | 3.1417 | 2.2137 | 1.2757 | 0.32873 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HULL SOUTH | 33 | 132 | Hull South | CREYKE BECK | HU3 5JA | PS (Best View Plan) | 88.0022 | 87.3902 | 86.7072 | 85.9712 | 85.1522 | 84.2762 | 83.4232 | 82.5922 | 81.7652 | 80.9472 | 77.5942 | 75.1282 | 73.6272 | 72.3082 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HULL WEST | 33 | 132 | Hull West | CREYKE BECK | HU13 0FA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HUMBERSTON | 33 | 132 | Humberston | GRIMSBY WEST | DN36 4AW | PS (Best View Plan) | 67.2121 | 66.6351 | 65.9051 | 65.3451 | 64.7921 | 64.1381 | 63.4801 | 62.8641 | 62.3291 | 61.7331 | 59.6021 | 57.7841 | 56.7231 | 55.8001 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HUNNINGLEY | 33 | 132 | Hunningley | WEST MELTON SECTION 3 | S70 3ET | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HUNSHELF | 66 | 132 | Hunshelf | WEST MELTON SECTION 3 | S36 8WR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | IMMINGHAM | 33 | 132 | Immingham | GRIMSBY WEST | DN40 1QT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KIRKHAW LANE | 33 | 132 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8SB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C 2/5 | 33 | 132 | Kirkstall C 2/5 | KIRKSTALL B | LS18 4EL | PS (Best View Plan) | 81.8482 | 81.7192 | 81.5742 | 81.4182 | 81.2442 | 81.0582 | 80.8782 | 80.7022 | 80.5282 | 80.3562 | 79.6572 | 79.1462 | 78.8422 | 78.5772 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS18 4EL | PS (Best View Plan) | 105.8955 | 104.8995 | 103.6915 | 102.6425 | 101.5495 | 100.3135 | 99.0895 | 97.9245 | 96.8555 | 95.7275 | 91.4655 | 88.0745 | 86.0915 | 84.3715 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS EAST | 33 | 132 | Leeds East | SKELTON GRANGE | LS9 6ED | PS (Best View Plan) | 65.4672 | 64.5592 | 63.3442 | 62.5712 | 61.8722 | 60.9802 | 60.0622 | 59.2252 | 58.5782 | 57.7832 | 55.2572 | 52.8122 | 51.4402 | 50.2592 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS NORTH | 33 | 132 | Leeds North | SKELTON GRANGE | LS7 2AU | PS (Best View Plan) | 107.591 | 107.181 | 106.723 | 106.229 | 105.678 | 105.09 | 104.519 | 103.963 | 103.412 | 102.868 | 100.654 | 99.039 | 98.075 | 97.237 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LINDLEY | 33 | 132 | Lindley | ELLAND | HD3 3NY | PS (Best View Plan) | 92.0602 | 91.1822 | 90.0612 | 89.2312 | 88.4222 | 87.4542 | 86.4772 | 85.5632 | 84.7842 | 83.9032 | 80.7952 | 78.0842 | 76.4992 | 75.1172 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LOW ROAD | 33 | 132 | Low Road | SKELTON GRANGE | LS10 1RH | PS (Best View Plan) | 1.462 | 1.092 | 0.66002 | 0.24602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MALLARD WAY | 33 | 132 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MENSTON | 33 | 132 | Menston | BRADFORD WEST | LS29 6BP | PS (Best View Plan) | 86.6197 | 85.5717 | 84.0147 | 83.3767 | 82.9857 | 82.2827 | 81.5007 | 80.8477 | 80.5567 | 79.9637 | 78.9317 | 77.0067 | 76.0237 | 75.1917 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MOSS ROAD | 33 | 132 | Moss Road | GRIMSBY WEST | DN32 0LW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 1/2 | 33 | 132 | Osgodby 1/2 | DRAX | YO8 5HY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 3/4 | 33 | 132 | Osgodby 3/4 | DRAX | YO8 5HY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY | 33 | 132 | Rodley | SKELTON GRANGE | LS13 1PZ | PS (Best View Plan) | 121.1771 | 120.1701 | 118.7851 | 117.9881 | 117.3121 | 116.4011 | 115.4491 | 114.5951 | 113.9871 | 113.1831 | 110.8311 | 108.3331 | 106.9551 | 105.7711 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | PS (Best View Plan) | 80.8518 | 80.3088 | 79.6918 | 79.0548 | 78.3548 | 77.5988 | 76.8598 | 76.1428 | 75.4398 | 74.7358 | 71.8898 | 69.7658 | 68.4798 | 67.3518 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SALTEND 132/33KV | 33 | 132 | Saltend 132/33kV | SALTEND NORTH | HU12 8EY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SANTON | 33 | 132 | Santon | KEADBY | DN16 1XP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE NORTH | 33 | 132 | Scunthorpe North | KEADBY | DN15 8GN | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE SOUTH | 33 | 132 | Scunthorpe South | KEADBY | DN16 1BD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SILSDEN | 33 | 132 | Silsden | BRADFORD WEST | BD20 0ND | PS (Best View Plan) | 0 | 51.0647 | 48.3837 | 46.8907 | 45.7047 | 44.0227 | 42.1767 | 40.4087 | 38.9937 | 37.0617 | 30.0037 | 22.2117 | 16.2347 | 10.4177 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EL | PS (Best View Plan) | 59.2604 | 58.5914 | 57.7704 | 57.0854 | 56.3854 | 55.5804 | 54.7744 | 54.0014 | 53.2924 | 52.5254 | 49.5834 | 47.1324 | 45.5834 | 44.1904 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | STAYGATE | 33 | 132 | Staygate | SKELTON GRANGE | BD6 1YA | PS (Best View Plan) | 115.6537 | 115.1537 | 114.5937 | 113.9917 | 113.3207 | 112.6027 | 111.9057 | 111.2277 | 110.5547 | 109.8907 | 107.1837 | 105.2057 | 104.0217 | 102.9897 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | THORNHILL 132KV | 33 | 132 | Thornhill 132kV | ELLAND | WF13 3JQ | PS (Best View Plan) | 19.0417 | 17.6447 | 15.7467 | 14.6077 | 13.6177 | 12.3117 | 10.9547 | 9.7267 | 8.8167 | 7.6507 | 4.0827 | 0.43974 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7AL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD NORTH | 33 | 132 | Wakefield North | SKELTON GRANGE | WF1 3HN | PS (Best View Plan) | 79.7204 | 78.2184 | 76.0554 | 75.0294 | 74.2864 | 73.1364 | 71.8934 | 70.8194 | 70.2014 | 69.2074 | 66.8904 | 63.7254 | 62.0404 | 60.6014 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WEST MELTON | 66 | 132 | West Melton | WEST MELTON SECTION 3 | S63 6EZ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WHINMOOR | 33 | 132 | Whinmoor | FERRYBRIDGE B | LS14 2DG | PS (Best View Plan) | 113.0483 | 111.5673 | 109.3763 | 108.4603 | 107.8833 | 106.8723 | 105.7513 | 104.8103 | 104.3743 | 103.5183 | 101.9553 | 99.1883 | 97.7693 | 96.5673 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WOLD NEWTON | 33 | 132 | Wold Newton | KEADBY | DN37 0SW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4JJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | ACKLAM | 11 | 33 | Bowesfield | NORTON | TS5 7LD | PS (Best View Plan) | 15.5764 | 15.3524 | 15.1024 | 14.8324 | 14.5304 | 14.2084 | 13.8974 | 13.5964 | 13.2994 | 13.0094 | 11.8444 | 11.0114 | 10.5404 | 10.1404 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | AMBERTON ROAD | 11 | 66 | Hartmoor | HARTMOOR | TS24 8PQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | ANNFIELD 66/20KV | 20 | 66 | Annfield | STELLA SOUTH | DH9 7XW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | ASHINGTON | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE63 8UJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE FORREST | 11 | 33 | Darlington North | NORTON | DL1 3NL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | Darlington North | NORTON | DL5 6HY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BARDEN FRIAR | 20 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5JR | PS (Best View Plan) | 7.577 | 7.563 | 7.546 | 7.529 | 7.509 | 7.488 | 7.467 | 7.446 | 7.425 | 7.405 | 7.318 | 7.252 | 7.209 | 7.17 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BEDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 1AH | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BELMONT | 11 | 66 | Potter House | SPENNYMOOR | DH1 2HL | PS (Best View Plan) | 2.6535 | 2.4675 | 2.2595 | 2.0355 | 1.7845 | 1.5165 | 1.2555 | 1.0015 | 0.75051 | 0.50151 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BENSHAM | 11 | 66 | Dunston | STELLA NORTH | NE8 2XY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.479 | 11.304 | 11.132 | 10.443 | 9.949 | 9.667 | 9.427 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BENTON SQUARE | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE12 9SR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BENWELL | 11 | 66 | Dunston | STELLA NORTH | NE4 8XQ | PS (Best View Plan) | 11.975 | 11.806 | 11.617 | 11.413 | 11.186 | 10.943 | 10.708 | 10.481 | 10.258 | 10.039 | 9.16 | 8.531 | 8.175 | 7.872 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | North Tees | NORTON | TS23 2AL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BILLY MILL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE29 8LP | PS (Best View Plan) | 17.2369 | 17.0859 | 16.9159 | 16.7339 | 16.5289 | 16.3119 | 16.1009 | 15.8969 | 15.6969 | 15.4999 | 14.7119 | 14.1479 | 13.8289 | 13.5579 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | PS (Best View Plan) | 32.5432 | 32.4242 | 32.2912 | 32.1492 | 31.9892 | 31.8182 | 31.6522 | 31.4912 | 31.3322 | 31.1752 | 30.5392 | 30.0772 | 29.8052 | 29.5702 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | PS (Best View Plan) | 24.1952 | 24.1212 | 24.0392 | 23.9502 | 23.8512 | 23.7452 | 23.6422 | 23.5422 | 23.4442 | 23.3482 | 22.9572 | 22.6762 | 22.5132 | 22.3732 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BLAYDON BURN | 11 | 66 | Dunston | STELLA NORTH | NE21 4BG | PS (Best View Plan) | 1.8 | 1.635 | 1.451 | 1.253 | 1.031 | 0.794 | 0.565 | 0.343 | 0.125 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER 33/11KV | 11 | 33 | Blucher | STELLA NORTH | NE15 9SB | PS (Best View Plan) | 14.3812 | 14.2222 | 14.0442 | 13.8522 | 13.6372 | 13.4082 | 13.1872 | 12.9732 | 12.7622 | 12.5562 | 11.7262 | 11.1332 | 10.7972 | 10.5122 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BOLDON DOWNHILL | 20 | 66 | West Boldon | WEST BOLDON | NE36 0AS | PS (Best View Plan) | 19.2055 | 19.0795 | 18.9385 | 18.7865 | 18.6165 | 18.4355 | 18.2595 | 18.0905 | 17.9235 | 17.7595 | 17.1025 | 16.6325 | 16.3655 | 16.1395 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | YO51 9NS | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 33/11KV | 11 | 33 | Bowesfield | NORTON | TS18 3HR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 66/11KV | 11 | 66 | North Tees | NORTON | TS23 1PX | PS (Best View Plan) | 39.2181 | 39.1141 | 38.9981 | 38.8731 | 38.7341 | 38.5851 | 38.4411 | 38.3011 | 38.1641 | 38.0291 | 37.4861 | 37.0971 | 36.8741 | 36.6841 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BRANCEPETH | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL15 0TW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BREAMISH STREET | 11 | 66 | West Boldon | WEST BOLDON | NE1 2BL | PS (Best View Plan) | 22.399 | 22.325 | 22.243 | 22.155 | 22.056 | 21.95 | 21.848 | 21.75 | 21.653 | 21.557 | 21.175 | 20.902 | 20.748 | 20.617 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | BRENDA TRADING | 11 | 66 | Hartmoor | HARTMOOR | TS25 1PD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CAMPLESHON ROAD | 11 | 33 | Melrosegate | OSBALDWICK | YO23 1HZ | PS (Best View Plan) | 0.2627 | 0.086703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CARLEY HILL | 11 | 66 | West Boldon | WEST BOLDON | SR5 1SG | PS (Best View Plan) | 19.386 | 19.181 | 18.951 | 18.704 | 18.427 | 18.131 | 17.846 | 17.57 | 17.298 | 17.031 | 15.961 | 15.196 | 14.762 | 14.394 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CARLIN HOW T3 T4 | 11 | 66 | Lackenby | LACKENBY | TS13 4DL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CARR HILL | 11 | 66 | West Boldon | WEST BOLDON | NE10 9SY | PS (Best View Plan) | 19.8009 | 19.5639 | 19.2989 | 19.0129 | 18.6939 | 18.3529 | 18.0229 | 17.7039 | 17.3899 | 17.0819 | 15.8429 | 14.9559 | 14.4499 | 14.0189 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CATTERICK CAMP | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL9 3HE | PS (Best View Plan) | 8.386 | 8.108 | 7.797 | 7.462 | 7.085 | 6.68 | 6.281 | 5.886 | 5.485 | 5.08 | 3.364 | 2.039 | 1.146 | 0.325 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CLOSE | 11 | 66 | Dunston | STELLA NORTH | NE1 3NB | PS (Best View Plan) | 12.689 | 12.603 | 12.506 | 12.402 | 12.285 | 12.161 | 12.04 | 11.924 | 11.809 | 11.697 | 11.247 | 10.926 | 10.744 | 10.59 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CONEYTHORPE | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG5 0RZ | PS (Best View Plan) | 6.7206 | 6.5876 | 6.4386 | 6.2786 | 6.0996 | 5.9076 | 5.7206 | 5.5376 | 5.3546 | 5.1736 | 4.4296 | 3.8776 | 3.5376 | 3.2366 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CONSETT | 20 | 66 | Annfield | STELLA SOUTH | DH8 7ND | PS (Best View Plan) | 7.482 | 7.192 | 6.867 | 6.518 | 6.126 | 5.707 | 5.3 | 4.903 | 4.509 | 4.119 | 2.525 | 1.356 | 0.65 | 0.031 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CORPORATION STREET | 11 | 33 | Barrack Road | STELLA NORTH | NE4 5SS | PS (Best View Plan) | 19.5255 | 19.4695 | 19.4065 | 19.3395 | 19.2635 | 19.1825 | 19.1045 | 19.0285 | 18.9545 | 18.8815 | 18.5895 | 18.3805 | 18.2615 | 18.1615 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | COWTON | 11 | 33 | Darlington Central | NORTON | DL6 2NF | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DARLEY | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 2PP | PS (Best View Plan) | 9.455 | 9.394 | 9.327 | 9.254 | 9.173 | 9.086 | 9.001 | 8.919 | 8.836 | 8.755 | 8.42 | 8.174 | 8.023 | 7.89 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 132/6KV | 6 | 132 | Darlington 132/6kV | NORTON | DL1 1SW | PS (Best View Plan) | 0 | 29.6274 | 29.5354 | 29.4354 | 29.3234 | 29.2044 | 29.0884 | 28.9764 | 28.8664 | 28.7574 | 28.3184 | 28.0014 | 27.8174 | 27.6594 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1SW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1HG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON EAST | 11 | 33 | Darlington Central | NORTON | DL1 4NP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON WEST | 11 | 33 | Darlington North | NORTON | DL3 9QG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DENWICK | 20 | 66 | Linton | BLYTH 132kV | NE66 3RG | PS (Best View Plan) | 5.631 | 5.308 | 4.946 | 4.557 | 4.119 | 3.65 | 3.191 | 2.739 | 2.285 | 1.83 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/11KV | 11 | 66 | Dunston | STELLA NORTH | NE11 9DH | PS (Best View Plan) | 1.2713 | 1.1723 | 1.0623 | 0.94328 | 0.81028 | 0.66928 | 0.53128 | 0.39928 | 0.26828 | 0.14028 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/20KV | 20 | 66 | Dunston | STELLA NORTH | NE11 9DH | PS (Best View Plan) | 11.84 | 11.661 | 11.462 | 11.246 | 11.005 | 10.749 | 10.5 | 10.26 | 10.023 | 9.79 | 8.857 | 8.188 | 7.806 | 7.482 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | DURHAM EAST | 11 | 66 | Potter House | SPENNYMOOR | DH1 5SU | PS (Best View Plan) | 22.0228 | 21.9318 | 21.8308 | 21.7228 | 21.6008 | 21.4708 | 21.3448 | 21.2228 | 21.1018 | 20.9818 | 20.4968 | 20.1448 | 19.9378 | 19.7578 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | EASTFIELD | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 3BY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.8449 | 20.6029 | 20.3629 | 19.3729 | 18.6389 | 18.1839 | 17.7799 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | EASTGATE CEMENT | 20 | 66 | Toronto | SPENNYMOOR | DL13 2LA | PS (Best View Plan) | 11.597 | 11.539 | 11.475 | 11.405 | 11.327 | 11.244 | 11.163 | 11.084 | 11.006 | 10.929 | 10.617 | 10.389 | 10.253 | 10.136 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | Barrack Road | STELLA NORTH | NE5 4JQ | PS (Best View Plan) | 22.6249 | 22.5299 | 22.4239 | 22.3099 | 22.1829 | 22.0469 | 21.9149 | 21.7879 | 21.6619 | 21.5399 | 21.0469 | 20.6949 | 20.4949 | 20.3259 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | ELVINGTON | 11 | 33 | Melrosegate | OSBALDWICK | YO41 4DY | PS (Best View Plan) | 0.9047 | 0.8627 | 0.8147 | 0.7627 | 0.7047 | 0.6427 | 0.5827 | 0.5247 | 0.4667 | 0.4097 | 0.1767 | 0.0077027 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | FARADAY STREET | 11 | 66 | North Tees | NORTON | TS1 4JG | PS (Best View Plan) | 12.9988 | 12.7778 | 12.5308 | 12.2648 | 11.9668 | 11.6488 | 11.3418 | 11.0458 | 10.7528 | 10.4668 | 9.3178 | 8.4978 | 8.0328 | 7.6388 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | Blyth 66kV | BLYTH 66KV | NE3 2SW and NE13 6BH | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | FISHBURN | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | TS29 6JQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH CENTRAL | 11 | 33 | Flatworth | TYNEMOUTH | NE29 7SH | PS (Best View Plan) | 30.5997 | 30.5057 | 30.4007 | 30.2877 | 30.1607 | 30.0257 | 29.8957 | 29.7687 | 29.6447 | 29.5227 | 29.0347 | 28.6857 | 28.4877 | 28.3197 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | FOSS ISLANDS | 11 | 33 | Melrosegate | OSBALDWICK | YO31 7US | PS (Best View Plan) | 1.1597 | 0.9447 | 0.7037 | 0.4437 | 0.1527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | FOSSWAY 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE6 4AN | PS (Best View Plan) | 14.2139 | 14.0219 | 13.8079 | 13.5769 | 13.3179 | 13.0429 | 12.7759 | 12.5179 | 12.2649 | 12.0159 | 11.0179 | 10.3049 | 9.8999 | 9.5569 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | FYLANDS BRIDGE | 11 | 66 | Toronto | SPENNYMOOR | DL14 9TA | PS (Best View Plan) | 9.77 | 9.546 | 9.296 | 9.026 | 8.723 | 8.4 | 8.086 | 7.78 | 7.476 | 7.176 | 5.951 | 5.055 | 4.515 | 4.044 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | GALE LANE | 11 | 33 | Poppleton | POPPLETON | YO24 3AF | PS (Best View Plan) | 7.618 | 7.449 | 7.261 | 7.059 | 6.832 | 6.59 | 6.356 | 6.129 | 5.905 | 5.685 | 4.797 | 4.158 | 3.79 | 3.474 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | GARWOOD STREET | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 5DQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.2046 | 19.9736 | 19.7466 | 18.8356 | 18.1846 | 17.8156 | 17.5036 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD CENTRAL | 11 | 33 | Barrack Road | STELLA NORTH | NE8 1HB | PS (Best View Plan) | 16.8398 | 16.7588 | 16.6668 | 16.5688 | 16.4588 | 16.3408 | 16.2268 | 16.1168 | 16.0088 | 15.9028 | 15.4758 | 15.1708 | 14.9968 | 14.8498 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD EAST | 11 | 66 | West Boldon | WEST BOLDON | NE8 3AH | PS (Best View Plan) | 22.609 | 22.595 | 22.58 | 22.564 | 22.546 | 22.527 | 22.509 | 22.491 | 22.473 | 22.456 | 22.387 | 22.337 | 22.309 | 22.285 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE3 1RR | PS (Best View Plan) | 30.439 | 30.366 | 30.285 | 30.197 | 30.099 | 29.995 | 29.894 | 29.796 | 29.7 | 29.605 | 29.226 | 28.956 | 28.802 | 28.672 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | GRANGETOWN | 11 | 66 | Lackenby | LACKENBY | TS6 7AS | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | GREATHAM | 11 | 132 | Greatham | SALTHOLME | TS25 2DD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | Lackenby | LACKENBY | TS14 6GQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HARLOW GREEN | 11 | 66 | West Boldon | WEST BOLDON | NE9 6NT | PS (Best View Plan) | 14.2541 | 14.0491 | 13.8191 | 13.5721 | 13.2961 | 13.0011 | 12.7161 | 12.4401 | 12.1681 | 11.9011 | 10.8301 | 10.0621 | 9.6241 | 9.2521 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HARMIRE BRIDGE | 20 | 66 | Toronto | SPENNYMOOR | DL12 8QJ | PS (Best View Plan) | 8.182 | 8.02 | 7.838 | 7.642 | 7.423 | 7.189 | 6.961 | 6.739 | 6.518 | 6.3 | 5.409 | 4.755 | 4.36 | 4.014 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HARRATON | 11 | 132 | Harraton | STELLA SOUTH | NE38 9BZ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.391 | 36.207 | 36.026 | 35.298 | 34.779 | 34.484 | 34.234 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/11KV | 11 | 132 | Harrogate 132/11kV | KNARESBOROUGH | HG1 2BN | PS (Best View Plan) | 27.332 | 26.967 | 26.558 | 26.118 | 25.625 | 25.097 | 24.583 | 24.081 | 23.58 | 23.083 | 21.036 | 19.521 | 18.585 | 17.756 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE WEST | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 0QB | PS (Best View Plan) | 32.497 | 32.402 | 32.295 | 32.181 | 32.052 | 31.915 | 31.781 | 31.65 | 31.52 | 31.39 | 30.859 | 30.467 | 30.226 | 30.013 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HARTMOOR 66/20KV | 20 | 66 | Hartmoor | HARTMOOR | TS27 3BL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HAWTHORN PIT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 9NX | PS (Best View Plan) | 10.189 | 9.9 | 9.577 | 9.229 | 8.839 | 8.422 | 8.018 | 7.626 | 7.238 | 6.856 | 5.304 | 4.179 | 3.516 | 2.943 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | Melrosegate | OSBALDWICK | YO31 8FZ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN | 6 | 66 | West Boldon | WEST BOLDON | NE31 1BD | PS (Best View Plan) | 0 | 4.8068 | 4.7628 | 4.7148 | 4.6628 | 4.6058 | 4.5518 | 4.4988 | 4.4468 | 4.3958 | 4.1918 | 4.0468 | 3.9638 | 3.8938 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN WEST | 11 | 66 | West Boldon | WEST BOLDON | NE31 1NA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HEDWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE32 4SW | PS (Best View Plan) | 0.27929 | 0.15829 | 0.02329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HEIGHINGTON | 11 | 33 | Darlington North | NORTON | DL5 6JW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HEXHAM | 20 | 66 | Coalburns | STELLA SOUTH | NE46 4NT | PS (Best View Plan) | 27.8779 | 27.7259 | 27.5569 | 27.3739 | 27.1689 | 26.9489 | 26.7339 | 26.5209 | 26.3069 | 26.0929 | 25.1939 | 24.5109 | 24.0649 | 23.6609 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HIGH BARMSTON | 11 | 66 | West Boldon | WEST BOLDON | NE38 8QA | PS (Best View Plan) | 20.626 | 20.487 | 20.33 | 20.162 | 19.973 | 19.772 | 19.578 | 19.39 | 19.205 | 19.024 | 18.295 | 17.775 | 17.479 | 17.229 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HIGH FLATTS | 11 | 66 | Potter House | SPENNYMOOR | DH2 2LR | PS (Best View Plan) | 21.1712 | 20.9512 | 20.7052 | 20.4412 | 20.1442 | 19.8272 | 19.5182 | 19.2182 | 18.9212 | 18.6262 | 17.4262 | 16.5482 | 16.0202 | 15.5602 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HOUGHTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | DH4 5HP | PS (Best View Plan) | 3.6651 | 3.4801 | 3.2731 | 3.0491 | 2.8001 | 2.5331 | 2.2741 | 2.0241 | 1.7761 | 1.5331 | 0.54714 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HOWDON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 0JX | PS (Best View Plan) | 4.3075 | 4.2575 | 4.2015 | 4.1415 | 4.0745 | 4.0035 | 3.9345 | 3.8675 | 3.8015 | 3.7375 | 3.4785 | 3.2935 | 3.1885 | 3.0995 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HUNTINGTON NEW LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO32 9TA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | Husthwaite | KNARESBOROUGH | YO61 4PN | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | JARROW | 11 | 33 | South Shields | SOUTH SHIELDS | NE32 5LD | PS (Best View Plan) | 18.3816 | 18.3386 | 18.2916 | 18.2396 | 18.1826 | 18.1216 | 18.0626 | 18.0056 | 17.9496 | 17.8946 | 17.6736 | 17.5156 | 17.4256 | 17.3496 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | KENTON | 11 | 33 | Blucher | STELLA NORTH | NE3 4UP | PS (Best View Plan) | 3.0931 | 2.9601 | 2.8111 | 2.6501 | 2.4711 | 2.2791 | 2.0941 | 1.9141 | 1.7381 | 1.5651 | 0.8711 | 0.3751 | 0.093103 | -0.1459 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | KIELDER | 20 | 33 | Spadeadam 33kV | SPADEADAM | NE48 1BH | PS (Best View Plan) | 4.041 | 4.026 | 4.008 | 3.99 | 3.969 | 3.947 | 3.926 | 3.904 | 3.883 | 3.862 | 3.774 | 3.708 | 3.667 | 3.63 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | KILLINGWORTH | 11 | 33 | Gosforth | TYNEMOUTH | NE12 6QQ | PS (Best View Plan) | 11.493 | 11.371 | 11.234 | 11.087 | 10.922 | 10.747 | 10.577 | 10.413 | 10.252 | 10.093 | 9.458 | 9.004 | 8.746 | 8.528 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | KIRBYMOORSIDE | 11 | 66 | Malton Grid | OSBALDWICK | YO62 6EZ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | LINTON 66/20KV | 20 | 66 | Linton | BLYTH 132kV | NE61 3AX | PS (Best View Plan) | 7.271 | 7.145 | 7.004 | 6.852 | 6.681 | 6.498 | 6.318 | 6.141 | 5.962 | 5.782 | 5.028 | 4.454 | 4.076 | 3.732 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | LONGBENTON | 11 | 33 | Gosforth | TYNEMOUTH | NE7 7LR | PS (Best View Plan) | 19.4522 | 19.2962 | 19.1212 | 18.9342 | 18.7232 | 18.4992 | 18.2822 | 18.0722 | 17.8662 | 17.6642 | 16.8522 | 16.2712 | 15.9422 | 15.6632 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | LOW SPENNYMOOR | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL16 7RS | PS (Best View Plan) | 7.91 | 7.78 | 7.633 | 7.475 | 7.299 | 7.11 | 6.926 | 6.747 | 6.57 | 6.394 | 5.678 | 5.154 | 4.838 | 4.562 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | LYNEMOUTH | 20 | 66 | Linton | BLYTH 132kV | NE61 5XH | PS (Best View Plan) | 6.051 | 6.02 | 5.986 | 5.948 | 5.907 | 5.862 | 5.818 | 5.774 | 5.73 | 5.686 | 5.499 | 5.357 | 5.263 | 5.177 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MADDISON STREET | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE24 1HD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MALLEABLE | 11 | 66 | North Tees | NORTON | TS18 2NR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1759 | 0.99788 | 0.82388 | 0.12188 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MALTON | 11 | 66 | Malton Grid | OSBALDWICK | YO17 6BT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MEADOWFIELD | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH7 8ER | PS (Best View Plan) | 0.835 | 0.763 | 0.682 | 0.595 | 0.497 | 0.393 | 0.291 | 0.192 | 0.095 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 33/11KV | 11 | 33 | Melrosegate | OSBALDWICK | YO31 0YB | PS (Best View Plan) | 1.5847 | 1.4807 | 1.3647 | 1.2397 | 1.0987 | 0.9497 | 0.8047 | 0.6647 | 0.5267 | 0.3907 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MILLBANK LANE | 11 | 33 | Bowesfield | NORTON | TS17 0AX | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5382 | 18.3022 | 18.0712 | 17.1372 | 16.4672 | 16.0822 | 15.7532 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MONKSEATON | 11 | 33 | Chirton Grange | TYNEMOUTH | NE25 9AF | PS (Best View Plan) | 19.2352 | 18.9952 | 18.7262 | 18.4362 | 18.1112 | 17.7642 | 36.667 | 36.341 | 36.018 | 35.7 | 34.411 | 33.477 | 32.927 | 32.453 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MOOR MONKTON PUMPS | 11 | 33 | Poppleton | POPPLETON | YO30 1BY | PS (Best View Plan) | 13.3899 | 13.3659 | 13.3389 | 13.3109 | 13.2779 | 13.2439 | 13.2099 | 13.1779 | 13.1449 | 13.1119 | 12.9759 | 12.8749 | 12.8119 | 12.7549 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MORPETH | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE61 6JH | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | MOUNT ROAD | 11 | 33 | Offerton | OFFERTON | SR4 7LJ | PS (Best View Plan) | 23.9282 | 23.7332 | 23.5132 | 23.2772 | 23.0132 | 22.7322 | 22.4592 | 22.1962 | 21.9372 | 21.6832 | 20.6632 | 19.9332 | 19.5202 | 19.1692 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | NEWBURN HAUGH | 11 | 132 | Newburn Haugh | STELLA NORTH | NE15 8SF | PS (Best View Plan) | 20.4034 | 20.3454 | 20.2804 | 20.2104 | 20.1314 | 20.0484 | 19.9674 | 19.8894 | 19.8124 | 19.7374 | 19.4344 | 19.2184 | 19.0954 | 18.9914 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | NEWBY | 11 | 33 | Scarborough Grid | OSBALDWICK | YO12 6NL | PS (Best View Plan) | 0.093868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | NEWCASTLE AIRPORT | 11 | 33 | Blucher | STELLA NORTH | NE13 8DF | PS (Best View Plan) | 27.0453 | 26.9343 | 26.8113 | 26.6783 | 26.5283 | 26.3683 | 26.2123 | 26.0603 | 25.9073 | 25.7563 | 25.1313 | 24.6663 | 24.3763 | 24.1193 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | Darlington North | NORTON | DL5 6EA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | NORTH STREET | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 1DU | PS (Best View Plan) | 1.2984 | 1.1614 | 1.0074 | 0.8424 | 0.6574 | 0.4604 | 0.2674 | 0.079403 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T1 T2 | 11 | 66 | North Tees | NORTON | TS23 1PX | PS (Best View Plan) | 22.2844 | 22.2254 | 22.1594 | 22.0874 | 22.0074 | 21.9224 | 21.8404 | 21.7604 | 21.6824 | 21.6054 | 21.2974 | 21.0774 | 20.9524 | 20.8464 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T3 T4 | 11 | 66 | North Tees | NORTON | TS23 1PY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1537 | 8.0107 | 7.8697 | 7.3057 | 6.9017 | 6.6717 | 6.4767 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | NORTHALLERTON | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 0QE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | NORTON 132/11KV | 11 | 132 | Norton 132/11kV | NORTON | TS21 1EG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | OATLANDS | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 8BY | PS (Best View Plan) | 18.1918 | 18.0578 | 17.9078 | 17.7468 | 17.5658 | 17.3718 | 17.1828 | 16.9988 | 16.8148 | 16.6318 | 15.8788 | 15.3198 | 14.9738 | 14.6668 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | OFFERTON 33/11KV | 11 | 33 | Offerton | OFFERTON | SR4 9NR | PS (Best View Plan) | 26.4388 | 26.2448 | 26.0288 | 25.7958 | 25.5348 | 25.2568 | 24.9878 | 24.7268 | 24.4708 | 24.2188 | 23.2058 | 22.4788 | 22.0638 | 21.7108 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | PALLION TRADING | 11 | 33 | Offerton | OFFERTON | SR4 6SN | PS (Best View Plan) | 13.4748 | 13.3098 | 13.1248 | 12.9248 | 12.7018 | 12.4638 | 12.2338 | 12.0118 | 11.7928 | 11.5778 | 10.7158 | 10.0998 | 9.7498 | 9.4538 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2HR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE WEST | 11 | 66 | Hartmoor | HARTMOOR | DH6 2RA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | PILGRIM | 11 | 33 | Barrack Road | STELLA NORTH | NE1 2LA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6142 | 3.5682 | 3.5222 | 3.3392 | 3.2092 | 3.1352 | 3.0722 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | Potter House | SPENNYMOOR | DH1 5FF | PS (Best View Plan) | 4.326 | 4.086 | 3.817 | 3.528 | 3.204 | 2.858 | 2.522 | 2.194 | 1.868 | 1.547 | 0.23305 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | Potter House | SPENNYMOOR | DH1 5FF | PS (Best View Plan) | 26.1972 | 26.1582 | 26.1152 | 26.0682 | 26.0152 | 25.9592 | 25.9052 | 25.8522 | 25.7992 | 25.7472 | 25.5362 | 25.3822 | 25.2912 | 25.2112 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | PRISSICK | 11 | 66 | Lackenby | LACKENBY | TS4 3SG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSCAR | 11 | 33 | Scarborough Grid | OSBALDWICK | YO13 0LZ | PS (Best View Plan) | 10.009 | 9.993 | 9.974 | 9.955 | 9.933 | 9.91 | 9.887 | 9.864 | 9.842 | 9.82 | 9.73 | 9.664 | 9.623 | 9.587 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | RAWCLIFFE LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO30 5SW | PS (Best View Plan) | 0.7367 | 0.5837 | 0.4127 | 0.2287 | 0.022703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | REDCAR | 11 | 66 | Lackenby | LACKENBY | TS10 2PA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | RESERVOIR | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE22 5QP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T1 | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL10 5BJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T2 | 11 | 33 | Darlington North | NORTON | DL10 5BJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | RIPON | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG4 1QE | PS (Best View Plan) | 14.1929 | 13.9519 | 13.6829 | 17.35 | 17.025 | 16.678 | 16.339 | 16.008 | 15.679 | 15.352 | 14.008 | 13.014 | 12.402 | 11.862 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | RISE CARR | 6 | 33 | Darlington North | NORTON | DL3 0RP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | ROMANBY | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 8HP | PS (Best View Plan) | 9.8931 | 9.7911 | 9.6761 | 9.5531 | 9.4151 | 9.2661 | 9.1211 | 8.9791 | 8.8361 | 8.6931 | 8.1001 | 7.6541 | 7.3691 | 7.1131 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | RUDBY | 11 | 33 | Bowesfield | NORTON | TS15 0JT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 2YH | PS (Best View Plan) | 2.011 | 1.789 | 1.54 | 1.273 | 0.97402 | 0.65302 | 0.34102 | 0.035017 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SEGHILL | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 7EY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | Husthwaite | KNARESBOROUGH | YO7 3NT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SEVERUS HILL | 11 | 33 | Poppleton | POPPLETON | YO26 4RR | PS (Best View Plan) | 0.65757 | 0.51457 | 0.35557 | 0.18357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SHERIFF HUTTON | 11 | 66 | Malton Grid | OSBALDWICK | YO60 6QN | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SHOTTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2EL | PS (Best View Plan) | 1.2332 | 1.0832 | 0.91517 | 0.73417 | 0.53117 | 0.31417 | 0.10317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SIMONSIDE | 11 | 33 | South Shields | SOUTH SHIELDS | NE34 9PD | PS (Best View Plan) | 13.1151 | 12.9981 | 12.8681 | 12.7271 | 12.5691 | 12.4021 | 12.2391 | 12.0821 | 11.9281 | 11.7761 | 11.1691 | 10.7341 | 10.4881 | 10.2791 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SKELDERGATE | 11 | 33 | Poppleton | POPPLETON | YO1 6HN | PS (Best View Plan) | 2.0349 | 1.9509 | 1.8579 | 1.7579 | 1.6459 | 1.5259 | 1.4099 | 1.2969 | 1.1869 | 1.0779 | 0.64088 | 0.32688 | 0.14688 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SKERNESIDE | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL5 6JH | PS (Best View Plan) | 0.13562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SPENCERBECK | 11 | 66 | Lackenby | LACKENBY | TS3 8TE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5JX | PS (Best View Plan) | 0.56567 | 0.37167 | 0.15467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | STARBECK | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 7PT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | STOKESLEY | 11 | 33 | Bowesfield | NORTON | TS9 5HS | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | STONEY CUT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 8RQ | PS (Best View Plan) | 15.7262 | 15.5352 | 15.3222 | 15.0932 | 14.8352 | 14.5602 | 14.2932 | 14.0332 | 13.7752 | 13.5202 | 12.4782 | 11.7162 | 11.2572 | 10.8572 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T1 T2 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | PS (Best View Plan) | 20.8893 | 20.7353 | 20.5633 | 20.3783 | 20.1713 | 19.9503 | 19.7373 | 19.5303 | 19.3273 | 19.1283 | 18.3283 | 17.7563 | 17.4333 | 17.1583 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T5 T6 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | PS (Best View Plan) | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.799 | 22.799 | 22.799 | 22.799 | 22.799 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | TANFIELD | 11 | 66 | Annfield | STELLA SOUTH | DH9 9DB | PS (Best View Plan) | 0.45115 | 0.27515 | 0.07815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | TEAM VALLEY | 20 | 66 | Ravensworth | STELLA SOUTH | NE11 0SX | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.8301 | 44.7371 | 44.6451 | 44.2791 | 44.0161 | 43.8671 | 43.7411 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | Seal Sands | SALTHOLME | TS23 3NF | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | TEMPLE PARK | 11 | 66 | West Boldon | WEST BOLDON | NE34 8TH | PS (Best View Plan) | 19.9194 | 19.7244 | 19.5054 | 19.2694 | 19.0054 | 18.7244 | 18.4524 | 18.1894 | 17.9304 | 17.6764 | 16.6574 | 15.9284 | 15.5154 | 15.1654 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | THIRSK | 11 | 33 | Leeming Bar_Skeeby | NORTON | YO7 4NH | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | THORNTON DALE | 11 | 66 | Malton Grid | OSBALDWICK | YO18 7SJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO 66/20KV | 20 | 66 | Toronto | SPENNYMOOR | DL14 7RJ | PS (Best View Plan) | 7.96 | 7.731 | 7.474 | 7.198 | 6.888 | 6.557 | 6.236 | 5.923 | 5.613 | 5.307 | 4.059 | 3.147 | 2.602 | 2.126 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | TUNSTALL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR3 2BT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.1129 | 24.8039 | 24.4999 | 23.2819 | 22.4109 | 21.9159 | 21.4959 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE30 1JG | PS (Best View Plan) | 19.5435 | 19.3465 | 19.1265 | 18.8895 | 18.6245 | 18.3415 | 18.0675 | 17.8035 | 17.5435 | 17.2885 | 16.2645 | 15.5335 | 15.1195 | 14.7685 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | UNIVERSITY | 11 | 33 | Barrack Road | STELLA NORTH | NE2 4PZ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3957 | 10.3367 | 10.2787 | 10.0447 | 9.8777 | 9.7827 | 9.7027 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | URLAY NOOK | 11 | 33 | Bowesfield | NORTON | TS16 0QB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | USWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE37 3HY | PS (Best View Plan) | 21.547 | 21.466 | 21.375 | 21.277 | 21.167 | 21.05 | 20.937 | 20.828 | 20.72 | 20.615 | 20.191 | 19.888 | 19.716 | 19.57 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WALKER | 11 | 66 | West Boldon | WEST BOLDON | NE6 3PZ | PS (Best View Plan) | 14.4789 | 14.3079 | 14.1159 | 13.9089 | 13.6779 | 13.4309 | 13.1919 | 12.9609 | 12.7339 | 12.5119 | 11.6179 | 10.9789 | 10.6169 | 10.3089 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WANSBECK | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE22 7DH | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WARDLEY | 6 | 66 | West Boldon | WEST BOLDON | NE31 1LP | PS (Best View Plan) | 0 | 15.5924 | 15.4844 | 15.3674 | 15.2374 | 15.0984 | 14.9644 | 14.8344 | 14.7064 | 14.5814 | 14.0774 | 13.7164 | 13.5114 | 13.3374 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WARKWORTH | 20 | 66 | Linton | BLYTH 132kV | NE65 0YD | PS (Best View Plan) | 6.201 | 5.951 | 5.671 | 5.37 | 5.031 | 4.668 | 4.312 | 3.961 | 3.607 | 3.253 | 1.769 | 0.643 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WENSLEYDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5ED | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WEST HARTFORD | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 3JP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WEST SOUTHWICK | 11 | 66 | West Boldon | WEST BOLDON | SR5 3TX | PS (Best View Plan) | 20.565 | 20.463 | 20.349 | 20.226 | 20.089 | 19.942 | 19.8 | 19.663 | 19.528 | 19.396 | 18.865 | 18.485 | 18.269 | 18.086 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WEST WYLAM | 20 | 66 | Coalburns | STELLA SOUTH | NE42 5EX | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WESTERHOPE | 11 | 33 | Blucher | STELLA NORTH | NE5 5HH | PS (Best View Plan) | 18.9463 | 18.8033 | 18.6423 | 18.4693 | 18.2753 | 18.0693 | 17.8693 | 17.6763 | 17.4853 | 17.2993 | 16.5513 | 16.0153 | 15.7123 | 15.4543 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WESTOE | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 3GE | PS (Best View Plan) | 13.045 | 12.891 | 12.718 | 12.531 | 12.323 | 12.1 | 11.885 | 11.677 | 11.472 | 11.272 | 10.466 | 9.891 | 9.564 | 9.288 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO22 4JE | PS (Best View Plan) | 11.7531 | 11.7091 | 11.6591 | 11.6051 | 11.5451 | 11.4801 | 11.4171 | 11.3561 | 11.2951 | 11.2341 | 10.9851 | 10.8011 | 10.6891 | 10.5891 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO22 4JE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO21 1LY | PS (Best View Plan) | 11.6689 | 11.6139 | 11.5519 | 11.4859 | 11.4109 | 11.3319 | 11.2539 | 11.1789 | 11.1029 | 11.0279 | 10.7199 | 10.4919 | 10.3519 | 10.2279 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO21 1LY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WILLINGTON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 7HS | PS (Best View Plan) | 18.4272 | 18.2722 | 18.0982 | 17.9112 | 17.7022 | 17.4782 | 17.2632 | 17.0542 | 16.8492 | 16.6482 | 15.8402 | 15.2622 | 14.9352 | 14.6582 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | Wormald Green 132/11kV | KNARESBOROUGH | HG3 3PS | PS (Best View Plan) | 13.047 | 12.935 | 12.809 | 12.673 | 12.52 | 12.357 | 12.199 | 12.043 | 11.889 | 11.735 | 11.104 | 10.637 | 10.348 | 10.093 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | WYNYARD | 11 | 66 | Hartmoor | HARTMOOR | TS2 2FB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | YEDINGHAM | 11 | 66 | Malton Grid | OSBALDWICK | YO17 8RR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | YORK UNIVERSITY | 11 | 33 | Melrosegate | OSBALDWICK | YO10 5ZF | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ABBEY ROAD | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS5 3NF | PS (Best View Plan) | 1.7903 | 1.7023 | 1.6043 | 1.4993 | 1.3823 | 1.2563 | 1.1353 | 1.0163 | 0.89933 | 0.78333 | 0.31133 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | AIREDALE ROAD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 4LJ | PS (Best View Plan) | 13.0276 | 12.9636 | 12.8936 | 12.8176 | 12.7326 | 12.6416 | 12.5536 | 12.4676 | 12.3826 | 12.2986 | 11.9566 | 11.7066 | 11.5566 | 11.4266 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ALDHAM | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S73 8SW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ALFRED GELDER STREET | 11 | 33 | Hull South | CREYKE BECK | HU1 1EP | PS (Best View Plan) | 2.8489 | 2.8149 | 2.7769 | 2.7359 | 2.6909 | 2.6419 | 2.5949 | 2.5489 | 2.5039 | 2.4599 | 2.2829 | 2.1569 | 2.0839 | 2.0229 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T1 | 11 | 33 | Leeds East | SKELTON GRANGE | LS7 3QB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T2 | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 3QB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ALVERTHORPE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 9PB | PS (Best View Plan) | 21.5313 | 21.3533 | 21.1553 | 20.9413 | 20.7023 | 20.4483 | 20.2003 | 19.9593 | 19.7203 | 19.4843 | 18.5213 | 17.8163 | 17.3923 | 17.0233 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ARMOURIES DRIVE | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LT | PS (Best View Plan) | 7.079 | 7.038 | 6.992 | 6.943 | 6.888 | 6.829 | 6.772 | 6.717 | 6.662 | 6.608 | 6.387 | 6.226 | 6.13 | 6.046 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ARMTHORPE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3DY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ARUNDEL STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4PJ | PS (Best View Plan) | 4.4168 | 4.3948 | 4.3708 | 4.3458 | 4.3168 | 4.2858 | 4.2558 | 4.2268 | 4.1978 | 4.1688 | 4.0528 | 3.9688 | 3.9178 | 3.8738 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ASKERN | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN6 0BY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | AUDBY LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 7SU | PS (Best View Plan) | 3.4264 | 3.2704 | 3.0964 | 2.9084 | 2.6994 | 2.4764 | 2.2594 | 2.0464 | 1.8354 | 1.6254 | 0.76538 | 0.13138 | 0 | -0.60062 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | AUSTERFIELD | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN10 6HD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BAILIFF BRIDGE | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 4DT | PS (Best View Plan) | 1.2325 | 1.1455 | 1.0485 | 0.94448 | 0.82848 | 0.70448 | 0.58248 | 0.46348 | 0.34348 | 0.22448 | 0 | 0 | 0 | -1.1065 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BALBY | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN4 8DG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BALME STREET | 11 | 33 | Bradford | BRADFORD WEST | BD1 4BA | PS (Best View Plan) | 3.2706 | 3.2076 | 3.1376 | 3.0626 | 2.9786 | 2.8886 | 2.8016 | 2.7166 | 2.6326 | 2.5496 | 2.2116 | 1.9636 | 1.8156 | 1.6866 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BARNBURGH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 9NT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BARNOLDSWICK | 11 | 33 | Silsden | BRADFORD WEST | BB18 5RU | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 7AU | PS (Best View Plan) | 32.1102 | 32.0492 | 31.9802 | 31.9072 | 31.8252 | 31.7372 | 31.6522 | 31.5692 | 31.4872 | 31.4062 | 31.0762 | 30.8352 | 30.6912 | 30.5662 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BARROW | 11 | 33 | Immingham | GRIMSBY WEST | DN19 7EG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 66/11KV | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1HT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BARWICK | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS15 8SW | PS (Best View Plan) | 13.0174 | 12.9024 | 12.7734 | 12.6344 | 12.4804 | 12.3144 | 12.1544 | 11.9984 | 11.8434 | 11.6914 | 11.0694 | 10.6154 | 10.3444 | 10.1094 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BASLOW ROAD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S17 3LT | PS (Best View Plan) | 0.15292 | 0.058919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BATLEY | 11 | 33 | Thornhill 132kV | ELLAND | WF17 6HU | PS (Best View Plan) | 4.7314 | 4.5754 | 4.4004 | 4.2134 | 4.0034 | 3.7804 | 3.5624 | 3.3504 | 3.1394 | 2.9304 | 2.0754 | 1.4464 | 1.0644 | 0.72942 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BEAL | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8DT | PS (Best View Plan) | 3.8351 | 3.7491 | 3.6551 | 3.5521 | 3.4401 | 3.3191 | 3.1991 | 3.0801 | 2.9601 | 2.8371 | 2.3181 | 1.9141 | 1.6391 | 1.3851 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | PS (Best View Plan) | 8.5465 | 8.5115 | 8.4735 | 8.4315 | 8.3855 | 8.3365 | 8.2885 | 8.2415 | 8.1955 | 8.1495 | 7.9635 | 7.8285 | 7.7475 | 7.6775 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | PS (Best View Plan) | 38.3592 | 38.2782 | 38.1862 | 38.0882 | 37.9792 | 37.8622 | 37.7482 | 37.6382 | 37.5282 | 37.4202 | 36.9802 | 36.6592 | 36.4682 | 36.3012 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BEIGHTON | 11 | 66 | Thurcroft | THURCROFT | S26 4TL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BELLHOUSE ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 0PL | PS (Best View Plan) | 1.2067 | 1.0557 | 0.88773 | 0.70573 | 0.50373 | 0.28773 | 0.078728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT AVENUE | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DF | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT COVERT | 11 | 33 | Wold Newton | KEADBY | LN11 9RA | PS (Best View Plan) | 0.0014624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BELTHORPE LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1SB | PS (Best View Plan) | 12.312 | 12.283 | 12.251 | 12.216 | 12.178 | 12.136 | 12.095 | 12.055 | 12.013 | 11.97 | 11.788 | 11.644 | 11.544 | 11.451 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BENTLEY | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN5 0NG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BILLET LANE | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BINBROOK | 11 | 33 | Wold Newton | KEADBY | LN8 6DR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 33/11KV | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | PS (Best View Plan) | 13.3126 | 13.1976 | 13.0686 | 12.9306 | 12.7766 | 12.6116 | 12.4516 | 12.2956 | 12.1406 | 11.9876 | 11.3636 | 10.9066 | 10.6326 | 10.3926 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BIRKBY | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 5HB | PS (Best View Plan) | 0.18455 | 0.064548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1HF | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BLUE BOY STREET | 11 | 33 | Neepsend | NEEPSEND | S3 7BA | PS (Best View Plan) | 1.341 | 1.318 | 1.291 | 1.263 | 1.231 | 1.198 | 1.165 | 1.133 | 1.102 | 1.07 | 0.94296 | 0.85096 | 0.79496 | 0.74696 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BOC BRINSWORTH | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1WT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BOLTON ROAD | 11 | 33 | Silsden | BRADFORD WEST | BD20 0JT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BOTTESFORD | 11 | 33 | Scunthorpe South | KEADBY | DN16 3UJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHOPE | 11 | 33 | Menston | BRADFORD WEST | LS16 9HA | PS (Best View Plan) | 0.72911 | 0.70011 | 0.66811 | 0.63311 | 0.59511 | 0.55411 | 0.51411 | 0.47511 | 0.43711 | 0.39911 | 0.24411 | 0.13211 | 0.06411 | 0.0061098 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BRAMLEY | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS13 3ST | PS (Best View Plan) | 21.5038 | 21.3448 | 21.1668 | 20.9748 | 20.7618 | 20.5328 | 20.3118 | 20.0958 | 19.8818 | 19.6708 | 18.8118 | 18.1848 | 17.8108 | 17.4858 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BRETT STREET | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 4HW | PS (Best View Plan) | 16.8605 | 16.5155 | 16.1305 | 15.7165 | 15.2625 | 14.7715 | 14.2865 | 13.7995 | 13.3005 | 12.7935 | 10.6015 | 8.8725 | 7.6535 | 6.5145 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BRIDGES ROAD | 11 | 33 | Scunthorpe South | KEADBY | DN17 1HA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1QE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BRODSWORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 7XB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BROOKFIELD STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LD | PS (Best View Plan) | 2.5329 | 2.5289 | 2.5239 | 2.5189 | 2.5139 | 2.5069 | 2.5019 | 2.4959 | 2.4899 | 2.4849 | 2.4619 | 2.4449 | 2.4349 | 2.4269 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BTP | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN31 2RL | PS (Best View Plan) | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3827 | 16.3827 | 16.3827 | 16.3827 | 16.3817 | 16.3817 | 16.3807 | 16.3807 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BURLEY STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS3 1JY | PS (Best View Plan) | 39.9601 | 39.9141 | 39.8631 | 39.8081 | 39.7471 | 39.6811 | 39.6171 | 39.5561 | 39.4941 | 39.4341 | 39.1871 | 39.0071 | 38.9001 | 38.8061 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BURMANTOFTS | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 7SS | PS (Best View Plan) | 10.2865 | 10.2505 | 10.2105 | 10.1665 | 10.1185 | 10.0665 | 10.0155 | 9.9665 | 9.9185 | 9.8705 | 9.6755 | 9.5325 | 9.4475 | 9.3735 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BURNLEYVILLE | 11 | 33 | Heckmondwike | SKELTON GRANGE | BD19 4RY | PS (Best View Plan) | 1.7804 | 1.6584 | 1.5224 | 1.3754 | 1.2114 | 1.0364 | 0.8674 | 0.7014 | 0.5364 | 0.3734 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BURTON PIDSEA | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU12 9AE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BURTON ROAD | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 2QG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 2HG | PS (Best View Plan) | 10.7243 | 10.6113 | 10.4853 | 10.3503 | 10.1983 | 10.0373 | 9.8803 | 9.7273 | 9.5753 | 9.4263 | 8.8183 | 8.3743 | 8.1093 | 7.8783 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | BUTTERWICK | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO17 8HF | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CAISTOR | 11 | 33 | Wold Newton | KEADBY | LN7 6RE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CALDER WHARF | 11 | 33 | Thornhill 132kV | ELLAND | WF13 3JQ | PS (Best View Plan) | 19.8008 | 19.6688 | 19.5218 | 19.3628 | 19.1858 | 18.9958 | 18.8118 | 18.6328 | 18.4538 | 18.2768 | 17.5538 | 17.0228 | 16.6998 | 16.4168 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CARLTON HILL | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 1JB | PS (Best View Plan) | 22.1734 | 22.1234 | 22.0684 | 22.0084 | 21.9424 | 21.8714 | 21.8024 | 21.7344 | 21.6684 | 21.6024 | 21.3354 | 21.1404 | 21.0234 | 20.9224 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CARR LANE | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 4PS | PS (Best View Plan) | 22.3617 | 22.2437 | 22.1117 | 21.9697 | 21.8107 | 21.6417 | 21.4767 | 21.3167 | 21.1577 | 21.0007 | 20.3597 | 19.8907 | 19.6087 | 19.3637 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CHELKER RESERVOIR | 11 | 33 | Silsden | BRADFORD WEST | LS29 0JS | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CHEVIN END | 11 | 33 | Menston | BRADFORD WEST | LS29 6BE | PS (Best View Plan) | 23.3545 | 23.2785 | 23.1935 | 23.1015 | 23.0005 | 22.8915 | 22.7855 | 22.6825 | 22.5805 | 22.4795 | 22.0685 | 21.7685 | 21.5895 | 21.4335 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CLARENCE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1JE | PS (Best View Plan) | 7.613 | 7.585 | 7.554 | 7.52 | 7.483 | 7.443 | 7.404 | 7.366 | 7.328 | 7.291 | 7.141 | 7.031 | 6.965 | 6.908 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON ROAD | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS2 9JT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON STREET | 11 | 33 | Hull South | CREYKE BECK | HU3 1AP | PS (Best View Plan) | 22.2309 | 22.1689 | 22.0989 | 22.0239 | 21.9409 | 21.8509 | 21.7649 | 21.6809 | 21.5989 | 21.5179 | 21.1939 | 20.9609 | 20.8279 | 20.7159 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CLAYWHEELS LANE | 11 | 33 | Neepsend | NEEPSEND | S6 1LY | PS (Best View Plan) | 22.4841 | 22.2861 | 22.0651 | 21.8271 | 21.5621 | 21.2791 | 21.0031 | 20.7361 | 20.4701 | 20.2081 | 19.1411 | 18.3621 | 17.8971 | 17.4921 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CLOUGH LANE | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3EH | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | COMMONSIDE LANE | 11 | 33 | Featherstone | FERRYBRIDGE B | WF7 5DF | PS (Best View Plan) | 5.2718 | 5.1658 | 5.0478 | 5.6198 | 5.4778 | 5.3268 | 5.1788 | 5.0358 | 4.8938 | 4.7528 | 4.1788 | 3.7588 | 3.5068 | 3.2878 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CONVAMORE ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN32 9PG | PS (Best View Plan) | 13.9683 | 13.8523 | 13.7223 | 13.5833 | 13.4283 | 13.2623 | 13.1003 | 12.9433 | 12.7873 | 12.6323 | 12.0013 | 11.5393 | 11.2603 | 11.0163 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CONYARD ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN35 7LQ | PS (Best View Plan) | 10.6086 | 10.4536 | 10.2816 | 10.0956 | 9.8886 | 9.6676 | 9.4526 | 9.2436 | 9.0356 | 8.8296 | 7.9896 | 7.3736 | 7.0016 | 6.6756 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CORNWALL STREET | 11 | 132 | Cornwall Street | CREYKE BECK | HU8 8AQ | PS (Best View Plan) | 32.3897 | 32.3297 | 32.2627 | 32.1907 | 32.1097 | 32.0227 | 31.9397 | 31.8587 | 31.7797 | 31.7007 | 31.3877 | 31.1627 | 31.0347 | 30.9257 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CORRINGHAM ROAD | 11 | 33 | Blyton | KEADBY | DN21 1FT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | COSTHORPE | 11 | 66 | Thurcroft | THURCROFT | S81 9QR | PS (Best View Plan) | 6.5931 | 6.5121 | 6.4221 | 6.3241 | 6.2161 | 6.1001 | 5.9871 | 5.8751 | 5.7611 | 5.6481 | 5.1721 | 4.8111 | 4.5731 | 4.3581 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | COUNTY ROAD NORTH | 11 | 33 | Hull South | CREYKE BECK | HU5 5DR | PS (Best View Plan) | 8.0954 | 7.8514 | 7.5774 | 7.2834 | 6.9564 | 6.6064 | 6.2654 | 5.9304 | 5.5954 | 5.2614 | 3.8794 | 2.8464 | 2.1954 | 1.6134 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CRACOE | 11 | 33 | Silsden | BRADFORD WEST | BD23 6BE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CROOKESMOOR ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 3FP | PS (Best View Plan) | 3.4497 | 3.2907 | 3.1137 | 2.9227 | 2.7097 | 2.4827 | 2.2617 | 2.0477 | 1.8347 | 1.6237 | 0.76771 | 0.14371 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CROSSHILLS | 11 | 33 | Silsden | BRADFORD WEST | BD20 7AQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CROWLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN17 4BB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | CROWN STREET | 11 | 33 | Girlington | BRADFORD WEST | BD1 2LA | PS (Best View Plan) | 0.76871 | 0.75171 | 0.73171 | 0.71171 | 0.68771 | 0.66371 | 0.63871 | 0.61571 | 0.59271 | 0.56971 | 0.47571 | 0.40771 | 0.36671 | 0.33071 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DALTON | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD2 1FF | PS (Best View Plan) | 2.566 | 2.389 | 2.192 | 1.979 | 1.743 | 1.49 | 1.244 | 1.004 | 0.765 | 0.529 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DARNALL | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 4JT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DEARNE ROAD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DEIGHTON | 11 | 33 | Brighouse 132/33kV | ELLAND | HD2 1UP | PS (Best View Plan) | 18.37 | 18.269 | 18.156 | 18.035 | 17.9 | 17.755 | 17.614 | 17.477 | 17.34 | 17.205 | 16.652 | 16.245 | 15.998 | 15.781 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DENBY DALE ROAD | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7BH | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DENBY GRANGE | 11 | 33 | Thornhill 132kV | ELLAND | WF4 4JG | PS (Best View Plan) | 0.29111 | 0.25411 | 0.21211 | 0.16711 | 0.11711 | 0.06311 | 0.01111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DENHOLME | 11 | 33 | Holmfield | BRADFORD WEST | BD13 4JF | PS (Best View Plan) | 11.5747 | 11.5387 | 11.4987 | 11.4557 | 11.4067 | 11.3557 | 11.3057 | 11.2567 | 11.2087 | 11.1607 | 10.9667 | 10.8257 | 10.7407 | 10.6667 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DINNINGTON | 11 | 66 | Thurcroft | THURCROFT | S25 3QT | PS (Best View Plan) | 0 | 22.1947 | 22.0217 | 21.8347 | 21.6277 | 21.4057 | 21.1897 | 20.9797 | 20.7707 | 20.5637 | 19.7177 | 19.0977 | 18.7217 | 18.3927 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DOUGHTY ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN32 0LR | PS (Best View Plan) | 3.7128 | 3.4958 | 3.2518 | 2.9898 | 2.6978 | 2.3858 | 2.0828 | 1.7868 | 1.4928 | 1.2028 | 0.016799 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DOWKER STREET | 11 | 33 | Lindley | ELLAND | HD3 4JB | PS (Best View Plan) | 0.44451 | 0.35151 | 0.24751 | 0.13651 | 0.012515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DRAX PRIMARY | 11 | 66 | Camblesforth | CAMBLESFORTH | YO8 6PQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 5XR | PS (Best View Plan) | 13.6115 | 13.2715 | 12.8915 | 12.4825 | 12.0335 | 11.5495 | 11.0705 | 10.5905 | 10.0975 | 9.5965 | 7.4325 | 5.7255 | 4.5225 | 3.3985 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DRONFIELD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S18 2XU | PS (Best View Plan) | 1.6382 | 1.5652 | 1.4832 | 1.3942 | 1.2972 | 1.1922 | 1.0892 | 0.9882 | 0.8862 | 0.7852 | 0.3622 | 0.042205 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DUDLEY HILL | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9NW | PS (Best View Plan) | 23.1088 | 23.0378 | 22.9588 | 22.8728 | 22.7768 | 22.6748 | 22.5758 | 22.4788 | 22.3828 | 22.2888 | 21.9028 | 21.6218 | 21.4528 | 21.3058 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DUNKESWICK | 11 | 33 | Bramham | FERRYBRIDGE B | LS17 9LP | PS (Best View Plan) | 11.9103 | 11.7573 | 11.5853 | 11.4003 | 11.1953 | 10.9753 | 10.7613 | 10.5503 | 10.3393 | 10.1303 | 9.2613 | 8.6123 | 8.2023 | 7.8363 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | DURKAR LOW LANE | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF4 3BJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | EASINGTON | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0SU | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | EASTFIELD ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ECCLESFIELD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 9YR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | EDLINGTON | 11 | 66 | Thurcroft | THURCROFT | DN12 1SU | PS (Best View Plan) | 13.4505 | 13.2675 | 13.0625 | 12.8425 | 12.5975 | 12.3355 | 12.0795 | 11.8285 | 11.5775 | 11.3275 | 10.2935 | 9.5215 | 9.0345 | 8.6005 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | EGGBOROUGH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | DN14 0QA | PS (Best View Plan) | 7.4016 | 7.3626 | 7.3186 | 7.2706 | 7.2186 | 7.1626 | 7.1066 | 7.0516 | 6.9946 | 6.9366 | 6.6866 | 6.4896 | 6.3516 | 6.2226 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ELGAR ROAD | 11 | 33 | Hull West | CREYKE BECK | HU4 7NY | PS (Best View Plan) | 21.7787 | 21.5087 | 21.2077 | 20.8847 | 20.5277 | 20.1427 | 19.7647 | 19.3887 | 19.0067 | 18.6207 | 16.9777 | 15.7047 | 14.8387 | 14.0407 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ELLAND 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX5 9AE | PS (Best View Plan) | 19.9315 | 19.8465 | 19.7505 | 19.6485 | 19.5345 | 19.4125 | 19.2935 | 19.1765 | 19.0585 | 18.9405 | 18.4495 | 18.0795 | 17.8405 | 17.6255 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ELLIFOOT LANE | 11 | 33 | Saltend 132/33kV | SALTEND NORTH | HU12 9EB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 1/3 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | PS (Best View Plan) | 4.7608 | 4.6978 | 4.6268 | 4.5508 | 4.4658 | 4.3748 | 4.2868 | 4.2018 | 4.1168 | 4.0328 | 3.6918 | 3.4418 | 3.2938 | 3.1638 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 2 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 1 | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 4LS | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 2 | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S75 4LS | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ELSECAR | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S74 8AU | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ENDIKE LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 8AY | PS (Best View Plan) | 16.4144 | 16.2604 | 16.0884 | 15.9024 | 15.6964 | 15.4764 | 15.2604 | 15.0484 | 14.8354 | 14.6234 | 13.7374 | 13.0704 | 12.6424 | 12.2584 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | EPWORTH | 11 | 33 | Blyton | KEADBY | DN9 1JU | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FARNLEY CRESCENT | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 5AN | PS (Best View Plan) | 0.75508 | 0.62908 | 0.48708 | 0.33508 | 0.16508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FENTON LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6EZ | PS (Best View Plan) | 5.0532 | 4.9932 | 4.9262 | 4.8542 | 4.7752 | 4.6902 | 4.6062 | 4.5222 | 4.4352 | 4.3472 | 3.9692 | 3.6702 | 3.4612 | 3.2662 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF11 8RR | PS (Best View Plan) | 1.967 | 1.694 | 1.388 | 1.06 | 0.695 | 0.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FIR TREE LANE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS17 7BZ | PS (Best View Plan) | 3.7558 | 3.5968 | 3.4188 | 3.2268 | 3.0128 | 2.7838 | 2.5618 | 2.3458 | 2.1308 | 1.9198 | 1.0588 | 0.43076 | 0.05576 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FIRST AVENUE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 9NE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FIRTH BROWN | 11 | 33 | Santon | KEADBY | DN16 1XP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FISH DAM LANE | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 3HQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FLIXBOROUGH | 11 | 33 | Scunthorpe North | KEADBY | DN15 8RR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FOLLY HALL | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 3TF | PS (Best View Plan) | 1.7547 | 1.6797 | 1.5957 | 1.5047 | 1.4037 | 1.2957 | 1.1907 | 1.0887 | 0.9867 | 0.8857 | 0.4737 | 0.1707 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FOUR LANE ENDS | 11 | 33 | Girlington | BRADFORD WEST | BD8 0LJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FOXHILLS | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FULLERTON ROAD | 11 | 33 | Templeborough 275/33KV | TEMPLEBOROUGH 275/33KV | S60 1DL | PS (Best View Plan) | 0.06487 | 0.0028698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | FURNESS AVENUE | 11 | 33 | Holmfield | BRADFORD WEST | WF8 3JA | PS (Best View Plan) | 1.0469 | 0.91386 | 0.76586 | 0.60686 | 0.43086 | 0.24186 | 0.056864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GAISBY LANE | 11 | 33 | Bradford | BRADFORD WEST | BD2 1BB | PS (Best View Plan) | 3.041 | 2.912 | 2.769 | 2.615 | 2.443 | 2.26 | 2.081 | 1.907 | 1.735 | 1.565 | 0.87198 | 0.36598 | 0.062984 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GIBRALTAR ROAD | 11 | 33 | Holmfield | BRADFORD WEST | HX1 4HL | PS (Best View Plan) | 4.2051 | 4.0221 | 3.8181 | 3.5991 | 3.3561 | 3.0951 | 2.8401 | 2.5881 | 2.3361 | 2.0831 | 1.0271 | 0.2281 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GIBSON LANE | 11 | 33 | Hull West | CREYKE BECK | HU14 3HH | PS (Best View Plan) | 16.888 | 16.631 | 16.345 | 16.037 | 15.699 | 15.334 | 14.973 | 14.611 | 14.24 | 13.863 | 12.233 | 10.946 | 10.04 | 9.193 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GILDERSOME | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 7HW | PS (Best View Plan) | 0.60687 | 0.53487 | 0.45387 | 0.36687 | 0.26987 | 0.16687 | 0.066867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GLEADLESS VALLEY | 11 | 33 | Norton Lees | NORTON LEES | S14 1FP | PS (Best View Plan) | 1.682 | 1.551 | 1.404 | 1.246 | 1.069 | 0.88098 | 0.69798 | 0.51998 | 0.34298 | 0.16898 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GOOLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 6SX | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GRAINTHORPE | 11 | 33 | Wold Newton | KEADBY | LN11 7JU | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GREAT COATES | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN37 9PN | PS (Best View Plan) | 2.0421 | 1.8671 | 1.6711 | 1.4611 | 1.2261 | 0.97609 | 0.73209 | 0.49409 | 0.25809 | 0.025087 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GREENHILL | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 7RJ | PS (Best View Plan) | 0.81423 | 0.73623 | 0.64723 | 0.55323 | 0.44723 | 0.33423 | 0.22423 | 0.11723 | 0.010233 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS RD | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GRIMETHORPE | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S72 7BQ | PS (Best View Plan) | 15.4899 | 15.4099 | 15.3209 | 15.2239 | 15.1169 | 15.0029 | 14.8909 | 14.7819 | 14.6729 | 14.5649 | 14.1199 | 13.7909 | 13.5869 | 13.4069 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GROVE STREET | 11 | 33 | Lindley | ELLAND | HD1 2PB | PS (Best View Plan) | 13.6602 | 13.6342 | 13.6062 | 13.5752 | 13.5412 | 13.5042 | 13.4682 | 13.4342 | 13.3992 | 13.3652 | 13.2252 | 13.1222 | 13.0592 | 13.0042 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | GUARDIAN GLASS | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8GA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HACKENTHORPE | 11 | 66 | Thurcroft | THURCROFT | S12 4ET | PS (Best View Plan) | 24.1276 | 23.9946 | 23.8456 | 23.6856 | 23.5066 | 23.3156 | 23.1296 | 22.9496 | 22.7706 | 22.5936 | 21.8736 | 21.3486 | 21.0356 | 20.7626 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 33/11KV | 11 | 33 | Halifax 132/33kV | ELLAND | HX1 1XB | PS (Best View Plan) | 2.3276 | 2.2076 | 2.0736 | 1.9296 | 1.7696 | 1.5986 | 1.4306 | 1.2656 | 1.0996 | 0.93262 | 0.23862 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HALLAM STREET | 11 | 33 | Menston | BRADFORD WEST | LS20 8AG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HARDEN | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 1BG | PS (Best View Plan) | 6.1103 | 6.0713 | 6.0283 | 5.9823 | 5.9313 | 5.8763 | 5.8223 | 5.7703 | 5.7193 | 5.6683 | 5.4613 | 5.3093 | 5.2183 | 5.1393 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HARPSWELL | 11 | 33 | Blyton | KEADBY | DN21 5UT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HARWORTH | 11 | 66 | Thurcroft | THURCROFT | DN11 8JW | PS (Best View Plan) | 19.5045 | 19.4155 | 19.3165 | 19.2095 | 19.0915 | 18.9645 | 18.8405 | 18.7185 | 18.5955 | 18.4735 | 17.9605 | 17.5735 | 17.3235 | 17.0975 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 1 | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD22 9EP | PS (Best View Plan) | 13.6306 | 13.5716 | 13.5066 | 13.4356 | 13.3576 | 13.2736 | 13.1916 | 13.1126 | 13.0336 | 12.9556 | 12.6386 | 12.4076 | 12.2686 | 12.1486 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 2 | 11 | 33 | Silsden | BRADFORD WEST | BD22 9EP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HAXEY | 11 | 33 | Blyton | KEADBY | DN9 2LT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HAYTON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1RJ | PS (Best View Plan) | 0 | 0 | 0 | 15.7365 | 15.4905 | 15.2255 | 14.9625 | 14.6995 | 14.4305 | 14.1555 | 12.9705 | 12.0355 | 11.3775 | 10.7615 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HAZLEHEAD | 11 | 33 | Thornhill 132kV | ELLAND | S36 4HG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HEBDEN BRIDGE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 6LX | PS (Best View Plan) | 7.4667 | 7.4297 | 7.3887 | 7.3447 | 7.2957 | 7.2437 | 7.1917 | 7.1417 | 7.0907 | 7.0397 | 6.8277 | 6.6667 | 6.5627 | 6.4697 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HEDLEY CHASE | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 1YN | PS (Best View Plan) | 12.6728 | 12.6418 | 12.6078 | 12.5718 | 12.5308 | 12.4868 | 12.4448 | 12.4028 | 12.3618 | 12.3218 | 12.1578 | 12.0378 | 11.9658 | 11.9038 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HEDON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 8ED | PS (Best View Plan) | 11.4045 | 11.3945 | 11.3845 | 11.3735 | 11.3605 | 11.3475 | 11.3345 | 11.3225 | 11.3105 | 11.2985 | 11.2505 | 11.2155 | 11.1955 | 11.1795 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HEMSWORTH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 5BZ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 1 | 11 | 33 | Hull South | CREYKE BECK | HU4 6SP | PS (Best View Plan) | 0.81984 | 0.75584 | 0.68384 | 0.60684 | 0.52184 | 0.42984 | 0.33984 | 0.25084 | 0.15984 | 0.067839 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 2 | 11 | 33 | Hull West | CREYKE BECK | HU4 6SP | PS (Best View Plan) | 1.4475 | 1.3875 | 1.3195 | 1.2475 | 1.1675 | 1.0815 | 0.99652 | 0.91252 | 0.82752 | 0.74252 | 0.38052 | 0.10252 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HIBALDSTOW | 11 | 33 | Santon | KEADBY | DN21 4NH | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HICKLETON | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 0DE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HILLCREST | 11 | 33 | Leeds East | SKELTON GRANGE | LS8 3AA | PS (Best View Plan) | 3.3989 | 3.2459 | 3.0759 | 2.8919 | 2.6869 | 2.4679 | 2.2559 | 2.0489 | 1.8439 | 1.6419 | 0.81793 | 0.21693 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HOLBECK | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9SZ | PS (Best View Plan) | 3.97 | 3.853 | 3.723 | 3.582 | 3.425 | 3.258 | 3.095 | 2.937 | 2.78 | 2.625 | 1.995 | 1.535 | 1.261 | 1.022 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HOLDERNESS | 11 | 33 | Bransholme | CREYKE BECK | HU9 4AU | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 4BX | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 20.2495 | 20.1415 | 20.0325 | 19.9215 | 19.8085 | 19.3215 | 18.9375 | 18.6675 | 18.4155 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HONLEY | 11 | 33 | Lindley | ELLAND | HD9 6RU | PS (Best View Plan) | 10.3309 | 10.2079 | 10.0699 | 9.9219 | 9.7569 | 9.5799 | 9.4089 | 9.2409 | 9.0739 | 8.9099 | 8.2349 | 7.7389 | 7.4379 | 7.1729 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HOPE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S33 6RP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HORBURY | 11 | 33 | Thornhill 132kV | ELLAND | WF4 6EU | PS (Best View Plan) | 17.8573 | 17.7143 | 17.5553 | 17.3833 | 17.1923 | 16.9873 | 16.7883 | 16.5953 | 16.4023 | 16.2133 | 15.4383 | 14.8723 | 14.5323 | 14.2353 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HOUGHTON MAIN | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S72 0GX | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 33/11KV | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5NP | PS (Best View Plan) | 22.5806 | 22.3766 | 22.1496 | 21.9046 | 21.6356 | 21.3466 | 21.0606 | 20.7746 | 20.4826 | 20.1866 | 18.9166 | 17.9216 | 17.2316 | 16.5906 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HUMBER ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LZ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | HUNMANBY | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO14 0JY | PS (Best View Plan) | 20.0455 | 19.8255 | 19.5795 | 19.3165 | 19.0245 | 18.7115 | 18.4035 | 18.0985 | 17.7895 | 17.4795 | 16.1675 | 15.1615 | 14.4905 | 13.8765 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ICI FIBRES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4LT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | IDLE | 11 | 33 | Bradford | BRADFORD WEST | BD10 8SA | PS (Best View Plan) | 2.5481 | 2.4101 | 2.2541 | 2.0871 | 1.9011 | 1.7021 | 1.5091 | 1.3211 | 1.1341 | 0.95005 | 0.19905 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ILKLEY | 11 | 33 | Silsden | BRADFORD WEST | LS29 9BE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | INGS LANE | 11 | 33 | Silsden | BRADFORD WEST | BD23 1UP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | IVESON HOUSE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 6RF | PS (Best View Plan) | 20.7756 | 20.6326 | 20.4716 | 20.2986 | 20.1056 | 19.8986 | 19.6986 | 19.5036 | 19.3106 | 19.1196 | 18.3426 | 17.7766 | 17.4386 | 17.1446 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | JARRATT STREET | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN1 2BS | PS (Best View Plan) | 13.0298 | 12.9318 | 12.8218 | 12.7038 | 12.5728 | 12.4318 | 12.2948 | 12.1608 | 12.0258 | 11.8928 | 11.3388 | 10.9248 | 10.6638 | 10.4318 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KEDDINGTON ROAD | 11 | 33 | Wold Newton | KEADBY | LN11 0DE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KEIGHLEY | 11 | 132 | Keighley | BRADFORD WEST | BD21 5AJ | PS (Best View Plan) | 30.3639 | 30.2859 | 30.1989 | 30.1049 | 29.9999 | 29.8889 | 29.7799 | 29.6739 | 29.5689 | 29.4659 | 29.0439 | 28.7359 | 28.5509 | 28.3909 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KENMORE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 0XE | PS (Best View Plan) | 18.8329 | 18.7679 | 18.6959 | 18.6169 | 18.5299 | 18.4369 | 18.3459 | 18.2579 | 18.1699 | 18.0839 | 17.7309 | 17.4729 | 17.3179 | 17.1829 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KILLINGHALL ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD3 8HN | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KILNHURST | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S64 5TL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KING GEORGE DOCK | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5PL | PS (Best View Plan) | 23.854 | 23.847 | 23.839 | 23.83 | 23.821 | 23.811 | 23.801 | 23.792 | 23.782 | 23.773 | 23.736 | 23.71 | 23.695 | 23.682 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KIRK DRIVE | 11 | 33 | Menston | BRADFORD WEST | BD17 6SA | PS (Best View Plan) | 0.98938 | 0.89338 | 0.78738 | 0.67238 | 0.54538 | 0.40838 | 0.27538 | 0.14638 | 0.018381 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KIRK SANDALL | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 1QP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KIRKBURN | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 9EH | PS (Best View Plan) | 6.0892 | 6.0072 | 5.9162 | 5.8182 | 5.7102 | 5.5942 | 5.4792 | 5.3642 | 5.2472 | 5.1282 | 4.6192 | 4.2212 | 3.9442 | 3.6872 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KIVETON PARK | 11 | 66 | Thurcroft | THURCROFT | S26 6RP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | KNOSTROP | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0PJ | PS (Best View Plan) | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LEA ROAD | 11 | 33 | Blyton | KEADBY | DN21 1ND | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LEASOWE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 2EY | PS (Best View Plan) | 6.788 | 6.711 | 6.625 | 6.532 | 6.429 | 6.319 | 6.212 | 6.108 | 6.004 | 5.903 | 5.488 | 5.185 | 5.004 | 4.847 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LEDSTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF10 2AX | PS (Best View Plan) | 1.2288 | 1.1138 | 0.9858 | 0.8478 | 0.6948 | 0.5298 | 0.3708 | 0.2148 | 0.060795 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS ROAD | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 5AA | PS (Best View Plan) | 0.35349 | 0.30449 | 0.24949 | 0.19049 | 0.12449 | 0.054491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LEGRAMS MILL LANE | 11 | 33 | Girlington | BRADFORD WEST | BD7 2BA | PS (Best View Plan) | 21.1828 | 21.1028 | 21.0138 | 20.9178 | 20.8108 | 20.6958 | 20.5848 | 20.4768 | 20.3688 | 20.2628 | 19.8308 | 19.5158 | 19.3268 | 19.1618 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LEYLANDS ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS2 7QB | PS (Best View Plan) | 16.1332 | 16.1112 | 16.0862 | 16.0592 | 16.0282 | 15.9962 | 15.9652 | 15.9342 | 15.9042 | 15.8742 | 15.7532 | 15.6642 | 15.6112 | 15.5652 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LIVERSEDGE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF15 7NY | PS (Best View Plan) | 1.7149 | 1.6289 | 1.5319 | 1.4289 | 1.3129 | 1.1899 | 1.0689 | 0.95188 | 0.83588 | 0.72088 | 0.24888 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LOUTH | 11 | 33 | Wold Newton | KEADBY | LN11 0WA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LOW MOOR | 11 | 33 | Staygate | SKELTON GRANGE | BD12 0NG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LOWFIELDS | 11 | 33 | Brighouse 132/33kV | ELLAND | HX5 9DE | PS (Best View Plan) | 25.255 | 25.253 | 25.249 | 25.246 | 25.242 | 25.238 | 25.234 | 25.23 | 25.226 | 25.222 | 25.205 | 25.192 | 25.184 | 25.177 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | LOXLEY ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 6SJ | PS (Best View Plan) | 0.24226 | 0.23526 | 0.22626 | 0.21726 | 0.20726 | 0.19626 | 0.18526 | 0.17526 | 0.16426 | 0.15426 | 0.11326 | 0.083257 | 0.065257 | 0.049257 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MANCHESTER ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD5 0QL | PS (Best View Plan) | 3.0677 | 3.0437 | 3.0167 | 2.9877 | 2.9547 | 2.9207 | 2.8867 | 2.8547 | 2.8217 | 2.7897 | 2.6597 | 2.5647 | 2.5077 | 2.4577 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 1 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S12 2DL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 2 | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S12 2DL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MARKHAM GATES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 2FS | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MARMION ROAD | 11 | 33 | Norton Lees | NORTON LEES | S11 8TS | PS (Best View Plan) | 2.5128 | 2.3408 | 2.1478 | 1.9408 | 1.7098 | 1.4628 | 1.2228 | 0.9888 | 0.7578 | 0.5288 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MARSDEN ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN31 3SQ | PS (Best View Plan) | 4.9539 | 4.8689 | 4.7739 | 4.6719 | 4.5579 | 4.4359 | 4.3169 | 4.2019 | 4.0869 | 3.9739 | 3.5099 | 3.1699 | 2.9649 | 2.7859 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MARTONGATE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 6RX | PS (Best View Plan) | 0 | 0 | 0 | 18.3215 | 17.8915 | 17.4265 | 16.9675 | 16.5065 | 16.0335 | 15.5535 | 13.4775 | 11.8395 | 10.6855 | 9.6075 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MELTHAM | 11 | 33 | Lindley | ELLAND | HD9 4AL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MEXBOROUGH 1_2 | 11 | 66 | Thurcroft | THURCROFT | S64 0JD | PS (Best View Plan) | 24.453 | 24.197 | 23.91 | 23.602 | 23.259 | 22.892 | 22.534 | 22.183 | 21.832 | 21.483 | 20.037 | 18.959 | 18.28 | 17.675 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MIDDLETON TOWN STREET | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS10 3TQ | PS (Best View Plan) | 16.3 | 16.173 | 16.031 | 15.878 | 15.708 | 15.526 | 15.35 | 15.178 | 15.007 | 14.839 | 14.155 | 13.655 | 13.357 | 13.098 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MILLHOUSES | 11 | 33 | Jordanthorpe | JORDANTHORPE | S7 2QH | PS (Best View Plan) | 1.2305 | 1.1675 | 1.0975 | 1.0215 | 0.93752 | 0.84752 | 0.75952 | 0.67452 | 0.59052 | 0.50652 | 0.16752 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MILLROYD STREET | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1JZ | PS (Best View Plan) | 14.2317 | 14.1107 | 13.9757 | 13.8307 | 13.6697 | 13.4967 | 13.3277 | 13.1607 | 12.9937 | 12.8267 | 12.1287 | 11.6017 | 11.2627 | 10.9567 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MILTON PLACE | 11 | 33 | Wakefield North | SKELTON GRANGE | WF5 9EG | PS (Best View Plan) | 18.5497 | 18.3767 | 18.1827 | 17.9747 | 17.7417 | 17.4937 | 17.2517 | 17.0167 | 16.7827 | 16.5527 | 15.6107 | 14.9217 | 14.5067 | 14.1447 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MIRFIELD | 11 | 33 | Thornhill 132kV | ELLAND | WF14 8NF | PS (Best View Plan) | 19.461 | 19.306 | 19.134 | 18.947 | 18.74 | 18.518 | 18.303 | 18.093 | 17.883 | 17.677 | 16.83 | 16.207 | 15.829 | 15.497 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MONCKTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S71 4BG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MOOR ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS6 4BJ | PS (Best View Plan) | 23.1316 | 22.9666 | 22.7816 | 22.5836 | 22.3616 | 22.1246 | 21.8956 | 21.6716 | 21.4496 | 21.2316 | 20.3406 | 19.6906 | 19.3026 | 18.9656 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MOORSIDE ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD2 3RJ | PS (Best View Plan) | 20.1099 | 19.9639 | 19.8009 | 19.6259 | 19.4309 | 19.2219 | 19.0189 | 18.8209 | 18.6259 | 18.4319 | 17.6439 | 17.0679 | 16.7239 | 16.4239 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MORLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 9HS | PS (Best View Plan) | 19.7657 | 19.6407 | 19.5017 | 19.3517 | 19.1847 | 19.0057 | 18.8327 | 18.6637 | 18.4957 | 18.3307 | 17.6577 | 17.1677 | 16.8747 | 16.6197 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MOUNT STREET | 11 | 33 | Bradford | BRADFORD WEST | BD4 8TB | PS (Best View Plan) | 20.99 | 20.956 | 20.917 | 20.875 | 20.829 | 20.779 | 20.731 | 20.684 | 20.637 | 20.591 | 20.403 | 20.266 | 20.184 | 20.112 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | MYTHOLMROYD | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 8NE | PS (Best View Plan) | 13.7341 | 13.6671 | 13.5931 | 13.5121 | 13.4231 | 13.3281 | 13.2341 | 13.1421 | 13.0491 | 12.9571 | 12.5701 | 12.2771 | 12.0881 | 11.9171 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NAB LANE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 9NE | PS (Best View Plan) | 11.9506 | 11.8726 | 11.7866 | 11.6936 | 11.5896 | 11.4786 | 11.3706 | 11.2656 | 11.1606 | 11.0576 | 10.6336 | 10.3226 | 10.1336 | 9.9676 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NABWOOD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD18 4AA | PS (Best View Plan) | 13.3561 | 13.2441 | 13.1181 | 12.9831 | 12.8321 | 12.6711 | 12.5141 | 12.3621 | 12.2111 | 12.0621 | 11.4531 | 11.0091 | 10.7431 | 10.5121 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NATIONAL AVENUE | 11 | 33 | Hull South | CREYKE BECK | HU5 4JN | PS (Best View Plan) | 0.74237 | 0.67537 | 0.60137 | 0.52137 | 0.43137 | 0.33637 | 0.24437 | 0.15437 | 0.066373 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | Wincobank | WINCOBANK | S61 2DL | PS (Best View Plan) | 18.8702 | 18.7492 | 18.6142 | 18.4682 | 18.3062 | 18.1332 | 17.9652 | 17.8002 | 17.6372 | 17.4762 | 16.8162 | 16.3322 | 16.0382 | 15.7812 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NEW ORCHARD LANE | 11 | 66 | Thurcroft | THURCROFT | S66 9HY | PS (Best View Plan) | 1.1492 | 1.0452 | 0.92715 | 0.80115 | 0.66115 | 0.51115 | 0.36515 | 0.22315 | 0.081153 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NEWHALL ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 2RS | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2933 | 1.2483 | 1.2043 | 1.0233 | 0.8923 | 0.8133 | 0.7453 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 1 | 11 | 33 | Hull West | CREYKE BECK | HU15 2QU | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 2 | 11 | 33 | Osgodby 3/4 | DRAX | HU15 2QU | PS (Best View Plan) | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NINELANDS LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS25 2PE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NORFOLK PARK | 11 | 33 | Norton Lees | NORTON LEES | S2 3UU | PS (Best View Plan) | 0.52939 | 0.40039 | 0.25639 | 0.10239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NORMANBY | 11 | 33 | Blyton | KEADBY | LN8 2HQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NORMANTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF6 2JA | PS (Best View Plan) | 4.5197 | 4.3847 | 4.2337 | 4.0717 | 3.8907 | 3.6967 | 3.5087 | 3.3257 | 3.1437 | 2.9637 | 2.2317 | 1.6957 | 1.3737 | 1.0927 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NORTH AVENUE | 11 | 33 | Menston | BRADFORD WEST | LS21 1SX | PS (Best View Plan) | 19.1456 | 19.0336 | 18.9096 | 18.7756 | 18.6266 | 18.4666 | 18.3116 | 18.1606 | 18.0116 | 17.8636 | 17.2626 | 16.8236 | 16.5616 | 16.3336 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NORTH THORESBY | 11 | 33 | Wold Newton | KEADBY | DN36 5SB | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | NORWOOD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 9JR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | OAKES ROAD | 11 | 33 | Lindley | ELLAND | HD3 3EW | PS (Best View Plan) | 2.4498 | 2.3148 | 2.1638 | 2.0018 | 1.8208 | 1.6268 | 1.4388 | 1.2558 | 1.0738 | 0.89282 | 0.15382 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | OAKWOOD LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 3LF | PS (Best View Plan) | 19.5121 | 19.4121 | 19.3001 | 19.1801 | 19.0461 | 18.9031 | 18.7641 | 18.6291 | 18.4941 | 18.3621 | 17.8231 | 17.4301 | 17.1961 | 16.9921 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ODSAL | 11 | 33 | Staygate | SKELTON GRANGE | BD6 1BW | PS (Best View Plan) | 2.6126 | 2.4896 | 2.3526 | 2.2056 | 2.0406 | 1.8646 | 1.6946 | 1.5286 | 1.3636 | 1.2006 | 0.5376 | 0.053604 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | OLYMPIA MILLS | 11 | 33 | Osgodby 3/4 | DRAX | YO8 7AG | PS (Best View Plan) | 19.6371 | 19.4131 | 19.1631 | 18.8941 | 18.5981 | 18.2801 | 17.9641 | 17.6491 | 17.3251 | 16.9971 | 15.5791 | 14.4631 | 13.6801 | 12.9491 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ORGREAVE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 9NA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | OUTWOOD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF3 3TA | PS (Best View Plan) | 1.7357 | 1.5987 | 1.4447 | 1.2797 | 1.0957 | 0.89866 | 0.70766 | 0.52166 | 0.33666 | 0.15466 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | PARK HILL | 11 | 33 | Sheffield City | SHEFFIELD CITY | S2 5QY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2402 | 1.1702 | 1.1022 | 0.82223 | 0.61723 | 0.49523 | 0.38923 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | PARK ROAD | 11 | 33 | Thornhill 132kV | ELLAND | WF12 9LW | PS (Best View Plan) | 1.1138 | 1.0038 | 0.87983 | 0.74683 | 0.59783 | 0.43883 | 0.28483 | 0.13383 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | PARK STREET | 11 | 132 | Park Street | WEST MELTON / THORPE MARSH | S61 1TF | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | PASTURE ROAD SOUTH | 11 | 33 | Santon | KEADBY | DN18 5RX | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | PATRINGTON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0AD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 6BG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 2FL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | PLANGEO | 11 | 33 | Hull South | CREYKE BECK | HU3 6EG | PS (Best View Plan) | 3.4984 | 3.3624 | 3.2104 | 3.0474 | 2.8644 | 2.6694 | 2.4814 | 2.2984 | 2.1194 | 1.9424 | 1.2344 | 0.72637 | 0.43737 | 0.19137 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | POLLINGTON | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | DN14 0RR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0JG | PS (Best View Plan) | 1.7218 | 1.6888 | 1.6518 | 1.6118 | 1.5668 | 1.5198 | 1.4738 | 1.4288 | 1.3848 | 1.3408 | 1.1618 | 1.0318 | 0.95476 | 0.88676 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | POOL | 11 | 33 | Menston | BRADFORD WEST | LS21 1RP | PS (Best View Plan) | 16.3725 | 16.3425 | 16.3095 | 16.2735 | 16.2335 | 16.1905 | 16.1485 | 16.1075 | 16.0675 | 16.0275 | 15.8635 | 15.7425 | 15.6695 | 15.6045 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | PRINCE OF WALES | 11 | 33 | Featherstone | FERRYBRIDGE B | WF8 4PR | PS (Best View Plan) | 10.7795 | 10.6255 | 10.4525 | 10.2665 | 10.0595 | 9.8375 | 9.6225 | 9.4125 | 9.2045 | 8.9995 | 8.1615 | 7.5485 | 7.1805 | 6.8585 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | PROSPECT ROAD | 11 | 33 | Lindley | ELLAND | HD3 4UY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | QUEENS ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 2LZ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | QUEENSBURY | 11 | 33 | Holmfield | BRADFORD WEST | HX3 7TJ | PS (Best View Plan) | 25.4334 | 25.2694 | 25.0874 | 24.8904 | 24.6714 | 24.4374 | 24.2094 | 23.9854 | 23.7624 | 23.5404 | 22.6234 | 21.9424 | 21.5164 | 21.1384 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | RAWCLIFFE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8PQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | RAWDON | 11 | 33 | Rodley | SKELTON GRANGE | LS19 7BZ | PS (Best View Plan) | 23.8076 | 23.6956 | 23.5706 | 23.4356 | 23.2846 | 23.1236 | 22.9676 | 22.8156 | 22.6646 | 22.5166 | 21.9106 | 21.4686 | 21.2046 | 20.9756 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | Rawmarsh Road 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | Rawmarsh Road 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON ROAD | 11 | 33 | Girlington | BRADFORD WEST | BD1 3SH | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON SPRING ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 1PD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1408 | 3.0638 | 2.9878 | 2.6788 | 2.4538 | 2.3198 | 2.2028 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | REVILL LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 7QX | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ROCKWARE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4RH | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY LANE | 11 | 33 | Rodley | SKELTON GRANGE | LS13 1LJ | PS (Best View Plan) | 0.68921 | 0.56321 | 0.42121 | 0.26921 | 0.10021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ROMAN AVENUE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 2DY | PS (Best View Plan) | 20.4416 | 20.3366 | 20.2186 | 20.0916 | 19.9496 | 19.7986 | 19.6516 | 19.5086 | 19.3666 | 19.2266 | 18.6566 | 18.2416 | 17.9936 | 17.7776 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | ROYDS LANE | 11 | 33 | Wakefield North | SKELTON GRANGE | LS26 0BE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | PS (Best View Plan) | 11.8878 | 11.8468 | 11.8008 | 11.7518 | 11.6958 | 11.6368 | 11.5798 | 11.5238 | 11.4678 | 11.4128 | 11.1878 | 11.0218 | 10.9208 | 10.8328 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SAINT STREET | 11 | 33 | Girlington | BRADFORD WEST | BD7 4EH | PS (Best View Plan) | 12.3876 | 12.3156 | 12.2346 | 12.1486 | 12.0516 | 11.9476 | 11.8476 | 11.7496 | 11.6526 | 11.5576 | 11.1666 | 10.8816 | 10.7116 | 10.5626 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SALTERFORTH | 11 | 33 | Silsden | BRADFORD WEST | BB18 6JD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SALTERHEBBLE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX3 0QH | PS (Best View Plan) | 19.4866 | 19.3626 | 19.2256 | 19.0766 | 18.9126 | 18.7366 | 18.5646 | 18.3946 | 18.2236 | 18.0526 | 17.3396 | 16.7996 | 16.4506 | 16.1356 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SALTSHOUSE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU8 9HR | PS (Best View Plan) | 21.3072 | 21.2192 | 21.1212 | 21.0152 | 20.8962 | 20.7702 | 20.6482 | 20.5292 | 20.4132 | 20.2992 | 19.8392 | 19.5112 | 19.3232 | 19.1632 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SANDHILL LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO41 4DF | PS (Best View Plan) | 0.2827 | 0.2357 | 0.1827 | 0.1257 | 0.062702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SAXON ROAD | 11 | 33 | Norton Lees | NORTON LEES | S8 0XQ | PS (Best View Plan) | 2.1872 | 2.0642 | 1.9262 | 1.7782 | 1.6122 | 1.4352 | 1.2642 | 1.0972 | 0.93118 | 0.76818 | 0.10218 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SCARTHO | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN33 3JL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SCHOLES | 11 | 33 | Thornhill 132kV | ELLAND | HD9 1UG | PS (Best View Plan) | 0.84913 | 0.75813 | 0.65613 | 0.54613 | 0.42413 | 0.29413 | 0.16713 | 0.043129 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SCISSETT | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SCULCOATES A | 11 | 132 | Sculcoates A | CREYKE BECK | HU5 1DA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SEACROFT | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 1LU | PS (Best View Plan) | 13.148 | 13.064 | 12.969 | 12.867 | 12.753 | 12.632 | 12.514 | 12.399 | 12.285 | 12.173 | 11.716 | 11.382 | 11.183 | 11.01 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SEATON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU11 5RQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SELBY | 11 | 33 | Osgodby 3/4 | DRAX | YO8 8NB | PS (Best View Plan) | 0.38857 | 0.013572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SELBY ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS15 0QE | PS (Best View Plan) | 19.8916 | 19.7516 | 19.5946 | 19.4256 | 19.2366 | 19.0356 | 18.8396 | 18.6496 | 18.4606 | 18.2746 | 17.5166 | 16.9636 | 16.6336 | 16.3466 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SHARLSTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF4 1BE | PS (Best View Plan) | 11.9117 | 11.7407 | 11.5497 | 11.3447 | 11.1157 | 10.8707 | 10.6337 | 10.4017 | 10.1727 | 9.9457 | 9.0197 | 8.3427 | 7.9367 | 7.5817 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SHEPCOTE TINSLEY | 11 | 33 | Wincobank | WINCOBANK | S9 1RF | PS (Best View Plan) | 30.0977 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SHERBURN | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6PL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SHIPLEY | 11 | 33 | Bradford | BRADFORD WEST | DN21 5UT | PS (Best View Plan) | 25.8655 | 25.7765 | 25.6775 | 25.5705 | 25.4505 | 25.3235 | 25.1995 | 25.0795 | 24.9595 | 24.8415 | 24.3605 | 24.0095 | 23.7995 | 23.6165 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SHIRLAND LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3GD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SILVER STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 2DU | PS (Best View Plan) | 2.7493 | 2.7293 | 2.7073 | 2.6843 | 2.6583 | 2.6303 | 2.6033 | 2.5763 | 2.5503 | 2.5243 | 2.4193 | 2.3423 | 2.2973 | 2.2573 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SILVERWOOD | 11 | 66 | Thurcroft | THURCROFT | S65 4PR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SKILLINGS LANE | 11 | 33 | Hull West | CREYKE BECK | HU15 1EQ | PS (Best View Plan) | 2.2874 | 2.1634 | 2.0254 | 1.8764 | 1.7134 | 1.5374 | 1.3634 | 1.1894 | 1.0104 | 0.82739 | 0.041394 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SKIPTON | 11 | 33 | Silsden | BRADFORD WEST | BD23 2RR | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SLAITHWAITE | 11 | 33 | Lindley | ELLAND | HD7 6LS | PS (Best View Plan) | 0.72786 | 0.63686 | 0.53386 | 0.42386 | 0.30086 | 0.16986 | 0.041862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SLEDMERE GARTH | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 5DS | PS (Best View Plan) | 18.704 | 18.648 | 18.585 | 18.517 | 18.441 | 18.36 | 18.282 | 18.206 | 18.13 | 18.055 | 17.751 | 17.529 | 17.397 | 17.281 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SMITH STREET | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 2RY | PS (Best View Plan) | 12.6639 | 12.5739 | 12.4729 | 12.3639 | 12.2429 | 12.1129 | 11.9869 | 11.8639 | 11.7419 | 11.6219 | 11.1319 | 10.7739 | 10.5589 | 10.3709 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SMITHY GREEN | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SNAITHING PARK ROAD | 11 | 33 | Norton Lees | NORTON LEES | S10 3LJ | PS (Best View Plan) | 0.060323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SNELSINS LANE | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 3UH | PS (Best View Plan) | 16.2996 | 16.2146 | 16.1206 | 16.0186 | 15.9056 | 15.7846 | 15.6666 | 15.5516 | 15.4376 | 15.3246 | 14.8626 | 14.5236 | 14.3176 | 14.1376 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH ELMSALL | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 2JH | PS (Best View Plan) | 23.0724 | 22.9554 | 22.8254 | 22.6844 | 22.5284 | 22.3614 | 22.1984 | 22.0404 | 21.8834 | 21.7274 | 21.0924 | 20.6274 | 20.3474 | 20.1024 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH FERRIBY | 11 | 33 | Santon | KEADBY | DN18 6JL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH KIRKBY | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 3TJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH RESTON | 11 | 33 | Wold Newton | KEADBY | LN11 8JQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH STREET | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 1AH | PS (Best View Plan) | 7.5989 | 7.4969 | 7.3829 | 7.2599 | 7.1239 | 6.9769 | 6.8359 | 6.6969 | 6.5599 | 6.4249 | 5.8739 | 5.4709 | 5.2299 | 5.0199 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHGATE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 3BE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 18.7766 | 18.6106 | 18.4446 | 18.2736 | 18.0996 | 17.3506 | 16.7586 | 16.3416 | 15.9526 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHWOOD ROAD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU16 5AN | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EN | PS (Best View Plan) | 24.0912 | 23.9502 | 23.7932 | 23.6232 | 23.4352 | 23.2342 | 23.0372 | 22.8432 | 22.6482 | 22.4532 | 21.6382 | 21.0222 | 20.6232 | 20.2642 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SPARK MILL LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 0TT | PS (Best View Plan) | 5.6682 | 5.3772 | 5.0522 | 4.7042 | 4.3202 | 3.9072 | 3.4972 | 3.0872 | 2.6672 | 2.2402 | 0.39421 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SPENBOROUGH | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 5BT | PS (Best View Plan) | 16.4635 | 16.3375 | 16.1965 | 16.0445 | 15.8755 | 15.6935 | 15.5175 | 15.3465 | 15.1755 | 15.0065 | 14.3145 | 13.8055 | 13.4955 | 13.2245 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SPRING MILL STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD5 7HF | PS (Best View Plan) | 3.4538 | 3.3988 | 3.3378 | 3.2728 | 3.1998 | 3.1208 | 3.0458 | 2.9718 | 2.8978 | 2.8258 | 2.5308 | 2.3158 | 2.1868 | 2.0738 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | STAINFORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN7 5HG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | STAIRFOOT | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 5AD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | STANLEY STREET | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S3 8HG | PS (Best View Plan) | 3.0873 | 3.0493 | 3.0073 | 2.9623 | 2.9123 | 2.8583 | 2.8063 | 2.7553 | 2.7053 | 2.6553 | 2.4523 | 2.3053 | 2.2163 | 2.1403 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | STANNINGTON ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 5FH | PS (Best View Plan) | 1.6476 | 1.4636 | 1.2576 | 1.0366 | 0.78963 | 0.52663 | 0.27062 | 0.020625 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | STATION ROAD | 11 | 33 | Scunthorpe North | KEADBY | DN15 6BT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | STEVENSON ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 3XG | PS (Best View Plan) | 1.1752 | 1.1752 | 1.1742 | 1.1742 | 1.1742 | 1.1742 | 1.1732 | 1.1732 | 1.1732 | 1.1722 | 1.1712 | 1.1712 | 1.1702 | 1.1702 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | STOKE STREET | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3QN | PS (Best View Plan) | 0.145 | 0.144 | 0.143 | 0.142 | 0.141 | 0.139 | 0.138 | 0.137 | 0.136 | 0.134 | 0.129 | 0.126 | 0.124 | 0.122 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 132/11KV | 11 | 132 | Stourton 132/11kV | SKELTON GRANGE | LS10 1SP | PS (Best View Plan) | 1.2711 | 1.2681 | 1.2641 | 1.2601 | 1.2561 | 1.2511 | 1.2461 | 1.2421 | 1.2371 | 1.2331 | 1.2151 | 1.2021 | 1.1941 | 1.1871 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 33/11KV | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1AX | PS (Best View Plan) | 5.567 | 5.514 | 5.456 | 5.393 | 5.322 | 5.247 | 5.175 | 5.104 | 5.033 | 4.964 | 4.681 | 4.475 | 4.352 | 4.245 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | STOW | 11 | 33 | Blyton | KEADBY | LN1 2AJ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SWAN BANK LANE | 11 | 33 | Halifax 132/33kV | ELLAND | HX3 9XT | PS (Best View Plan) | 1.3343 | 1.2493 | 1.1543 | 1.0523 | 0.93935 | 0.81735 | 0.69935 | 0.58135 | 0.46335 | 0.34535 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SWEET STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9TZ | PS (Best View Plan) | 7.639 | 7.624 | 7.608 | 7.59 | 7.57 | 7.549 | 7.529 | 7.509 | 7.489 | 7.47 | 7.391 | 7.333 | 7.299 | 7.269 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | SWINNOW MOOR | 11 | 33 | Rodley | SKELTON GRANGE | LS13 4RJ | PS (Best View Plan) | 2.2665 | 2.1385 | 1.9955 | 1.8415 | 1.6705 | 1.4875 | 1.3095 | 1.1365 | 0.96447 | 0.79547 | 0.10647 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | TADCASTER | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9PA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | TANKERSLEY PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 2PT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S60 1AD | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | THORNBURY | 11 | 33 | Rodley | SKELTON GRANGE | BD3 7AD | PS (Best View Plan) | 4.9373 | 4.8383 | 4.7263 | 4.6063 | 4.4723 | 4.3303 | 4.1913 | 4.0563 | 3.9223 | 3.7893 | 3.2503 | 2.8573 | 2.6213 | 2.4163 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | THORNE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN8 4NA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | THORNTON | 11 | 33 | Holmfield | BRADFORD WEST | BD13 3DP | PS (Best View Plan) | 19.8402 | 19.6722 | 19.4842 | 19.2822 | 19.0562 | 18.8152 | 18.5802 | 18.3522 | 18.1262 | 17.9032 | 16.9932 | 16.3282 | 15.9292 | 15.5822 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | THORPE ROAD | 11 | 33 | Osgodby 3/4 | DRAX | DN14 7PA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | TICKHILL ROAD | 11 | 66 | Thurcroft | THURCROFT | S66 7QN | PS (Best View Plan) | 28.9414 | 28.7724 | 28.5844 | 28.3814 | 28.1564 | 27.9144 | 27.6794 | 27.4504 | 27.2214 | 26.9944 | 26.0624 | 25.3734 | 24.9494 | 24.5744 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | TINGLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | WF3 1SS | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY PARK ROAD | 11 | 33 | Wincobank | WINCOBANK | S9 5DL | PS (Best View Plan) | 2.8527 | 2.8457 | 2.8367 | 2.8277 | 2.8177 | 2.8067 | 2.7967 | 2.7857 | 2.7757 | 2.7657 | 2.7247 | 2.6957 | 2.6777 | 2.6617 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1TY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | TIVERTON ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 4DA | PS (Best View Plan) | 1.3801 | 1.2831 | 1.1751 | 1.0581 | 0.92814 | 0.78814 | 0.65314 | 0.52314 | 0.39514 | 0.26914 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | TODMORDEN | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | OL14 7NB | PS (Best View Plan) | 12.74 | 12.646 | 12.541 | 12.428 | 12.303 | 12.169 | 12.037 | 11.908 | 11.778 | 11.648 | 11.104 | 10.693 | 10.427 | 10.187 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | TOLLER LANE | 11 | 33 | Girlington | BRADFORD WEST | BD9 5LE | PS (Best View Plan) | 21.2052 | 21.1022 | 20.9872 | 20.8632 | 20.7242 | 20.5762 | 20.4332 | 20.2932 | 20.1542 | 20.0182 | 19.4602 | 19.0522 | 18.8082 | 18.5962 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | TONG STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9PP | PS (Best View Plan) | 3.2222 | 3.1672 | 3.1062 | 3.0402 | 2.9662 | 2.8882 | 2.8122 | 2.7372 | 2.6642 | 2.5912 | 2.2942 | 2.0782 | 1.9482 | 1.8352 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | UPPER BASINGHALL STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS1 5JS | PS (Best View Plan) | 4.33 | 4.321 | 4.311 | 4.301 | 4.289 | 4.276 | 4.264 | 4.252 | 4.24 | 4.229 | 4.181 | 4.146 | 4.126 | 4.108 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | VARLEY STREET | 11 | 33 | Rodley | SKELTON GRANGE | LS28 6AN | PS (Best View Plan) | 22.6104 | 22.4974 | 22.3704 | 22.2334 | 22.0814 | 21.9184 | 21.7604 | 21.6064 | 21.4544 | 21.3034 | 20.6914 | 20.2444 | 19.9774 | 19.7454 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | VICTORIA STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4DP | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42142 | 0.38742 | 0.35442 | 0.21842 | 0.12042 | 0.061419 | 0.010419 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WALESBY | 11 | 33 | Wold Newton | KEADBY | LN8 3UL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WARREN LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9NT | PS (Best View Plan) | 3.8558 | 3.8248 | 3.7908 | 3.7538 | 3.7128 | 3.6688 | 3.6258 | 3.5838 | 3.5418 | 3.5008 | 3.3308 | 3.2048 | 3.1278 | 3.0598 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WATH UPON DEARNE | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DX | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | Wincobank | WINCOBANK | S60 5BL | PS (Best View Plan) | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5026 | 30.5026 | 30.5026 | 30.5026 | 30.5016 | 30.5016 | 30.5016 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WAWNE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 5BT | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WEELAND ROAD | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 0LA | PS (Best View Plan) | 7.1271 | 7.0691 | 7.0041 | 31.0816 | 31.0036 | 30.9206 | 30.8396 | 30.7606 | 30.6826 | 30.6056 | 30.2896 | 30.0586 | 29.9196 | 29.7986 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WELLINGTON STREET | 11 | 33 | Featherstone | FERRYBRIDGE B | WF10 1NW | PS (Best View Plan) | 12.8601 | 12.7621 | 12.6531 | 12.5361 | 12.4051 | 12.2641 | 12.1281 | 11.9961 | 11.8641 | 11.7351 | 11.2051 | 10.8171 | 10.5851 | 10.3811 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WESLEY CRESCENT | 11 | 33 | Humberston | GRIMSBY WEST | DN35 0JU | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WEST DOCKS | 11 | 33 | Hull South | CREYKE BECK | HU3 4UU | PS (Best View Plan) | 1.7723 | 1.7683 | 1.7633 | 1.7583 | 1.7523 | 1.7453 | 1.7393 | 1.7333 | 1.7273 | 1.7213 | 1.6983 | 1.6823 | 1.6723 | 1.6643 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WEST END LANE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN11 0PU | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WEST MOOR PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3FE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WEST PARK | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 5PS | PS (Best View Plan) | 7.0156 | 6.9256 | 6.8246 | 6.7156 | 6.5946 | 6.4646 | 6.3386 | 6.2166 | 6.0946 | 5.9746 | 5.4876 | 5.1316 | 4.9196 | 4.7346 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WESTCOTT STREET | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU8 8JN | PS (Best View Plan) | 0.85689 | 0.69689 | 0.51789 | 0.32489 | 0.10989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WHEATACRE ROAD | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 2GQ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WHEATLEY PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4PG | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WHINGATE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 3QT | PS (Best View Plan) | 19.8291 | 19.7551 | 19.6711 | 19.5811 | 19.4811 | 19.3741 | 19.2701 | 19.1691 | 19.0691 | 18.9701 | 18.5671 | 18.2731 | 18.0971 | 17.9451 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WHITE LEE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 8AF | PS (Best View Plan) | 1.8215 | 1.6655 | 1.4915 | 1.3035 | 1.0945 | 0.8705 | 0.6535 | 0.4415 | 0.2305 | 0.021502 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | Low Road | SKELTON GRANGE | LS1 4HR | PS (Best View Plan) | 7.773 | 7.769 | 7.764 | 7.759 | 7.754 | 7.748 | 7.743 | 7.738 | 7.732 | 7.727 | 7.705 | 7.69 | 7.681 | 7.672 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS1 4BN | PS (Best View Plan) | 18.6989 | 18.6919 | 18.6849 | 18.6769 | 18.6689 | 18.6599 | 18.6509 | 18.6419 | 18.6339 | 18.6249 | 18.5909 | 18.5659 | 18.5509 | 18.5379 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WIBSEY | 11 | 33 | Staygate | SKELTON GRANGE | BD6 3BG | PS (Best View Plan) | 0.50726 | 0.36026 | 0.19526 | 0.019261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WITHERNSEA | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU19 2QA | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WOODCOCK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 5LL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WOODSEATS | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 8QB | PS (Best View Plan) | 2.1287 | 2.0117 | 1.8807 | 1.7407 | 1.5827 | 1.4157 | 1.2527 | 1.0937 | 0.93669 | 0.78169 | 0.14869 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WOOLLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 5JE | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WORSBROUGH PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S70 5LY | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | WRAWBY | 11 | 33 | Santon | KEADBY | DN20 8SX | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4BL | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | YEW GREEN ROAD | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD4 5DD | PS (Best View Plan) | 1.285 | 1.172 | 1.046 | 0.91097 | 0.75997 | 0.59897 | 0.44297 | 0.28997 | 0.13797 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | YORK ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 6TF | PS (Best View Plan) | 20.6901 | 20.5541 | 20.4021 | 20.2381 | 20.0561 | 19.8611 | 19.6721 | 19.4871 | 19.3051 | 19.1251 | 18.3911 | 17.8551 | 17.5361 | 17.2581 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgY | YORK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 3AZ | PS (Best View Plan) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg Planning Scenario | Network Capacity Generation Headroom (MVA)
NPgN | ANNFIELD | 66 | 132 | Annfield | STELLA SOUTH | DH9 7XW | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BARRACK ROAD | 33 | 132 | Barrack Road | STELLA NORTH | NE4 6DB | CT (DFES) | 114.536 | 114.353 | 114.074 | 113.756 | 113.315 | 112.699 | 112.066 | 111.416 | 110.691 | 109.902 | 105.535 | 101.453 | 97.255 | 93.208 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER | 33 | 132 | Blucher | STELLA NORTH | NE15 9SD | CT (DFES) | 94.396 | 93.899 | 93.151 | 92.476 | 91.552 | 90.201 | 88.819 | 87.43 | 85.95 | 84.343 | 75.913 | 67.157 | 58.446 | 49.928 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD | 33 | 132 | Bowesfield | NORTON | TS18 3HP | CT (DFES) | 63.036 | 61.553 | 58.644 | 57.057 | 55.4 | 52.894 | 50.238 | 47.72 | 45.476 | 42.714 | 30.381 | 17.105 | 4.329 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CHIRTON GRANGE | 33 | 132 | Chirton Grange | TYNEMOUTH | NE29 8EY | CT (DFES) | 61.877 | 61.425 | 60.773 | 60.103 | 59.158 | 57.796 | 56.404 | 54.992 | 53.45 | 51.79 | 42.864 | 33.85 | 24.791 | 16.025 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | COALBURNS | 66 | 132 | Coalburns | STELLA SOUTH | NE40 4JP | CT (DFES) | 71.496 | 70.236 | 67.49 | 66.368 | 65.487 | 64.069 | 62.499 | 61.108 | 60.191 | 58.776 | 54.194 | 48.527 | 43.509 | 36.907 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL | 33 | 132 | Darlington Central | NORTON | DL1 1HG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON NORTH | 33 | 132 | Darlington North | NORTON | DL3 0XE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON | 66 | 132 | Dunston | STELLA NORTH | NE11 9DH | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH | 33 | 132 | Flatworth | TYNEMOUTH | NE29 7FN | CT (DFES) | 27.216 | 26.991 | 26.682 | 26.345 | 25.859 | 25.158 | 24.445 | 23.72 | 22.925 | 22.076 | 17.492 | 12.829 | 8.149 | 3.645 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH | 33 | 132 | Gosforth | TYNEMOUTH | NE3 1XL | CT (DFES) | 88.766 | 88.356 | 87.785 | 87.172 | 86.294 | 85.028 | 83.738 | 82.429 | 80.993 | 79.458 | 71.178 | 62.775 | 54.338 | 46.207 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/33KV | 33 | 132 | Harrogate 132/33kV | KNARESBOROUGH | HG1 2LA | CT (DFES) | 45.968 | 45.476 | 44.663 | 44.011 | 43.166 | 41.933 | 40.654 | 39.369 | 38.022 | 36.519 | 28.728 | 20.759 | 12.804 | 4.896 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE | 33 | 132 | Husthwaite | KNARESBOROUGH | YO61 4PN | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | Leeming Bar_Skeeby | NORTON | DL7 0RL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LINTON | 66 | 132 | Linton | BLYTH 132kV | NE61 5DA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALTON GRID | 66 | 132 | Malton Grid | OSBALDWICK | YO17 6RD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 132/33kV | 33 | 132 | Melrosegate | OSBALDWICK | YO31 0YB | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES | 66 | 132 | North Tees | NORTON | TS23 1PY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE 132/66kV | 66 | 132 | Potter House | SPENNYMOOR | DH1 5FF | CT (DFES) | 89.699 | 88.822 | 87.237 | 86.159 | 84.877 | 82.989 | 81.016 | 79.074 | 77.143 | 74.913 | 63.85 | 52.519 | 41.297 | 29.854 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSWORTH | 66 | 132 | Ravensworth | STELLA SOUTH | DH3 1RQ | CT (DFES) | 76.495 | 76.208 | 75.677 | 75.319 | 74.899 | 74.286 | 73.644 | 73.013 | 72.391 | 71.666 | 68.072 | 64.472 | 60.891 | 57.228 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH GRID | 33 | 132 | Scarborough Grid | OSBALDWICK | YO11 2YH | CT (DFES) | 72.181 | 70.956 | 68.595 | 67.262 | 65.83 | 63.671 | 61.384 | 59.189 | 57.175 | 54.729 | 43.509 | 31.491 | 19.846 | 7.44 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEAL SANDS | 66 | 132 | Seal Sands | SALTHOLME | TS2 1FB | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5LJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO | 66 | 132 | Toronto | SPENNYMOOR | DL14 7RJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 3PS | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ATTERCLIFFE | 33 | 132 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3FA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 132/66KV | 66 | 132 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1LR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6NJ | CT (DFES) | 67.6024 | 66.8854 | 65.5874 | 64.8314 | 63.9454 | 62.4174 | 60.7654 | 59.1474 | 57.5864 | 55.7554 | 46.1044 | 35.6524 | 25.0614 | 14.5554 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEVERLEY 132/33KV | 33 | 132 | Beverley 132/33kV | CREYKE BECK | HU17 0RW | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 132/33KV | 33 | 132 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | CT (DFES) | 9.7336 | 9.3156 | 8.7646 | 8.1786 | 7.3296 | 6.0796 | 4.8006 | 3.4966 | 2.0626 | 0.53459 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS B | 33 | 132 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1DA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLYTON | 33 | 132 | Blyton | KEADBY | DN21 3NS | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRADFORD | 33 | 132 | Bradford | BRADFORD WEST | BD1 4RF | CT (DFES) | 99.451 | 98.926 | 98.257 | 97.508 | 96.409 | 94.807 | 93.171 | 91.5 | 89.65 | 87.687 | 77.005 | 65.582 | 54.01 | 42.702 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHAM | 33 | 132 | Bramham | FERRYBRIDGE B | LS24 9NT | CT (DFES) | 28.5527 | 26.7747 | 22.3107 | 21.3047 | 21.1597 | 19.6117 | 17.4777 | 15.6617 | 14.9397 | 13.1237 | 4.8607 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRANSHOLME | 33 | 132 | Bransholme | CREYKE BECK | HU7 4ZN | CT (DFES) | 65.8453 | 65.2483 | 64.1343 | 63.5303 | 62.8513 | 61.6423 | 60.3223 | 59.0373 | 57.8243 | 56.3763 | 48.7753 | 40.5313 | 32.1753 | 23.8613 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | Brighouse 132/33kV | ELLAND | HD6 1PZ | CT (DFES) | 96.2007 | 95.4697 | 94.0657 | 93.3617 | 92.6077 | 91.2097 | 89.6647 | 88.1687 | 86.7937 | 85.1167 | 76.3747 | 66.7937 | 57.0947 | 47.4087 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 8UX | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER CENTRAL | 33 | 132 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1RE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | Driffield/Beverley Group | CREYKE BECK | YO25 5NW | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FEATHERSTONE | 33 | 132 | Featherstone | FERRYBRIDGE B | WF7 6HE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIRLINGTON | 33 | 132 | Girlington | BRADFORD WEST | BD7 2NB | CT (DFES) | 85.1155 | 84.7985 | 84.3935 | 83.9405 | 83.2755 | 82.3065 | 81.3175 | 80.3065 | 79.1875 | 78.0005 | 71.5395 | 64.6315 | 57.6315 | 50.7925 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 132/33KV | 33 | 132 | Halifax 132/33kV | ELLAND | HX1 1XB | CT (DFES) | 1.3926 | 1.2186 | 0.99762 | 0.75062 | 0.39262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HECKMONDWIKE | 33 | 132 | Heckmondwike | SKELTON GRANGE | WF16 9LU | CT (DFES) | 88.65 | 88.286 | 87.821 | 87.301 | 86.542 | 85.435 | 84.304 | 83.146 | 81.861 | 80.496 | 73.054 | 65.124 | 57.08 | 49.217 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLMFIELD | 33 | 132 | Holmfield | BRADFORD WEST | HX2 9AY | CT (DFES) | 57.0045 | 56.4255 | 55.6905 | 54.8685 | 53.6695 | 51.9185 | 50.1245 | 48.2845 | 46.2365 | 44.0595 | 32.1825 | 19.4645 | 6.5745 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 132/33KV | 33 | 132 | Hull East 132/33kV | SALTEND NORTH | HU9 5NL | CT (DFES) | 8.4567 | 7.9717 | 7.3457 | 6.6537 | 5.6847 | 4.2827 | 2.8277 | 1.3087 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL SOUTH | 33 | 132 | Hull South | CREYKE BECK | HU3 5JA | CT (DFES) | 88.2412 | 87.7512 | 87.1242 | 86.4232 | 85.4012 | 83.9162 | 82.3972 | 80.8402 | 79.1122 | 77.2702 | 67.2172 | 56.5692 | 45.7522 | 35.1732 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL WEST | 33 | 132 | Hull West | CREYKE BECK | HU13 0FA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUMBERSTON | 33 | 132 | Humberston | GRIMSBY WEST | DN36 4AW | CT (DFES) | 67.5431 | 67.1461 | 66.5221 | 66.0301 | 65.3841 | 64.3801 | 63.3241 | 62.2611 | 61.1481 | 59.9061 | 53.2021 | 46.1521 | 38.9671 | 31.8931 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNNINGLEY | 33 | 132 | Hunningley | WEST MELTON SECTION 3 | S70 3ET | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNSHELF | 66 | 132 | Hunshelf | WEST MELTON SECTION 3 | S36 8WR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IMMINGHAM | 33 | 132 | Immingham | GRIMSBY WEST | DN40 1QT | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKHAW LANE | 33 | 132 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8SB | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C 2/5 | 33 | 132 | Kirkstall C 2/5 | KIRKSTALL B | LS18 4EL | CT (DFES) | 81.8982 | 81.7922 | 81.6582 | 81.5072 | 81.2872 | 80.9662 | 80.6382 | 80.3042 | 79.9332 | 79.5392 | 77.3912 | 75.1082 | 72.7912 | 70.5282 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS18 4EL | CT (DFES) | 106.3685 | 105.6085 | 104.5105 | 103.5115 | 102.1225 | 100.0215 | 97.8475 | 95.6475 | 93.2855 | 90.7205 | 76.8475 | 62.0375 | 47.0175 | 32.2875 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS EAST | 33 | 132 | Leeds East | SKELTON GRANGE | LS9 6ED | CT (DFES) | 66.0112 | 65.3772 | 64.3012 | 63.5832 | 62.6882 | 61.2182 | 59.6542 | 58.1032 | 56.5482 | 54.7752 | 45.3392 | 35.1752 | 24.8732 | 14.6952 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS NORTH | 33 | 132 | Leeds North | SKELTON GRANGE | LS7 2AU | CT (DFES) | 107.748 | 107.415 | 106.989 | 106.512 | 105.814 | 104.799 | 103.762 | 102.702 | 101.528 | 100.281 | 93.482 | 86.256 | 78.925 | 71.761 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LINDLEY | 33 | 132 | Lindley | ELLAND | HD3 3NY | CT (DFES) | 92.5262 | 91.8792 | 90.8652 | 90.0752 | 89.0302 | 87.3892 | 85.6662 | 83.9372 | 82.1342 | 80.1332 | 69.3832 | 57.8312 | 46.1222 | 34.5962 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOW ROAD | 33 | 132 | Low Road | SKELTON GRANGE | LS10 1RH | CT (DFES) | 1.622 | 1.332 | 0.93502 | 0.53802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MALLARD WAY | 33 | 132 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DB | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MENSTON | 33 | 132 | Menston | BRADFORD WEST | LS29 6BP | CT (DFES) | 87.4027 | 86.7547 | 85.4097 | 84.8527 | 84.3387 | 83.2637 | 82.0427 | 80.8897 | 79.9267 | 78.6687 | 72.2587 | 65.1827 | 58.0227 | 50.8107 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOSS ROAD | 33 | 132 | Moss Road | GRIMSBY WEST | DN32 0LW | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 1/2 | 33 | 132 | Osgodby 1/2 | DRAX | YO8 5HY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 3/4 | 33 | 132 | Osgodby 3/4 | DRAX | YO8 5HY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY | 33 | 132 | Rodley | SKELTON GRANGE | LS13 1PZ | CT (DFES) | 121.8151 | 121.1291 | 119.9081 | 119.1741 | 118.3001 | 116.8101 | 115.2051 | 113.6301 | 112.0941 | 110.3081 | 100.8681 | 90.6471 | 80.2921 | 70.0321 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | CT (DFES) | 81.0628 | 80.6218 | 80.0438 | 79.4228 | 78.5248 | 77.2058 | 75.8558 | 74.4758 | 72.9528 | 71.3288 | 62.4838 | 53.0518 | 43.4868 | 34.1278 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTEND 132/33KV | 33 | 132 | Saltend 132/33kV | SALTEND NORTH | HU12 8EY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SANTON | 33 | 132 | Santon | KEADBY | DN16 1XP | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE NORTH | 33 | 132 | Scunthorpe North | KEADBY | DN15 8GN | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE SOUTH | 33 | 132 | Scunthorpe South | KEADBY | DN16 1BD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILSDEN | 33 | 132 | Silsden | BRADFORD WEST | BD20 0ND | CT (DFES) | 0 | 52.7857 | 50.3927 | 48.9957 | 47.4927 | 44.8397 | 41.8527 | 38.7607 | 35.5927 | 31.7637 | 11.0187 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EL | CT (DFES) | 59.5594 | 59.0314 | 58.2624 | 57.5844 | 56.6544 | 55.2324 | 53.7494 | 52.2414 | 50.6194 | 48.8454 | 39.2444 | 28.9034 | 18.4214 | 8.1104 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAYGATE | 33 | 132 | Staygate | SKELTON GRANGE | BD6 1YA | CT (DFES) | 115.8327 | 115.4147 | 114.8807 | 114.2847 | 113.4087 | 112.1317 | 110.8287 | 109.4977 | 108.0237 | 106.4597 | 97.9477 | 88.8467 | 79.6257 | 70.6167 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNHILL 132KV | 33 | 132 | Thornhill 132kV | ELLAND | WF13 3JQ | CT (DFES) | 19.9137 | 18.9637 | 17.2987 | 16.2607 | 15.0087 | 12.9037 | 10.6437 | 8.4127 | 6.2107 | 3.6627 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7AL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD NORTH | 33 | 132 | Wakefield North | SKELTON GRANGE | WF1 3HN | CT (DFES) | 80.8164 | 79.8944 | 78.0634 | 77.2014 | 76.3294 | 74.6624 | 72.8004 | 71.0114 | 69.4194 | 67.4224 | 57.0474 | 45.8954 | 34.5514 | 23.1894 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST MELTON | 66 | 132 | West Melton | WEST MELTON SECTION 3 | S63 6EZ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHINMOOR | 33 | 132 | Whinmoor | FERRYBRIDGE B | LS14 2DG | CT (DFES) | 114.1443 | 113.2253 | 111.3303 | 110.5283 | 109.7713 | 108.2173 | 106.4583 | 104.7923 | 103.3843 | 101.5633 | 92.2523 | 81.9933 | 71.6093 | 61.1643 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOLD NEWTON | 33 | 132 | Wold Newton | KEADBY | DN37 0SW | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4JJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ACKLAM | 11 | 33 | Bowesfield | NORTON | TS5 7LD | CT (DFES) | 15.6814 | 15.5114 | 15.2864 | 15.0334 | 14.6624 | 14.1274 | 13.5834 | 13.0314 | 12.4224 | 11.7774 | 8.2864 | 4.7014 | 1.1114 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AMBERTON ROAD | 11 | 66 | Hartmoor | HARTMOOR | TS24 8PQ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ANNFIELD 66/20KV | 20 | 66 | Annfield | STELLA SOUTH | DH9 7XW | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ASHINGTON | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE63 8UJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE FORREST | 11 | 33 | Darlington North | NORTON | DL1 3NL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | Darlington North | NORTON | DL5 6HY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BARDEN FRIAR | 20 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5JR | CT (DFES) | 7.588 | 7.58 | 7.568 | 7.554 | 7.534 | 7.507 | 7.479 | 7.449 | 7.415 | 7.378 | 7.166 | 6.973 | 6.773 | 6.577 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BEDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 1AH | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BELMONT | 11 | 66 | Potter House | SPENNYMOOR | DH1 2HL | CT (DFES) | 2.7575 | 2.6325 | 2.4555 | 2.2555 | 1.9705 | 1.5625 | 1.1455 | 0.71651 | 0.23951 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENSHAM | 11 | 66 | Dunston | STELLA NORTH | NE8 2XY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.209 | 10.863 | 10.492 | 8.481 | 6.456 | 4.416 | 2.455 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENTON SQUARE | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE12 9SR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENWELL | 11 | 66 | Dunston | STELLA NORTH | NE4 8XQ | CT (DFES) | 12.059 | 11.936 | 11.769 | 11.582 | 11.31 | 10.918 | 10.52 | 10.114 | 9.667 | 9.19 | 6.603 | 3.984 | 1.351 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | North Tees | NORTON | TS23 2AL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BILLY MILL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE29 8LP | CT (DFES) | 17.3089 | 17.1949 | 17.0419 | 16.8719 | 16.6219 | 16.2609 | 15.8939 | 15.5219 | 15.1109 | 14.6759 | 12.3189 | 9.9029 | 7.4829 | 5.1589 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | CT (DFES) | 32.6012 | 32.5142 | 32.3972 | 32.2652 | 32.0732 | 31.7962 | 31.5142 | 31.2252 | 30.9062 | 30.5662 | 28.7172 | 26.8392 | 24.9512 | 23.1332 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | CT (DFES) | 24.2352 | 24.1842 | 24.1122 | 24.0322 | 23.9172 | 23.7532 | 23.5842 | 23.4132 | 23.2222 | 23.0182 | 21.9042 | 20.7962 | 19.6762 | 18.5982 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLAYDON BURN | 11 | 66 | Dunston | STELLA NORTH | NE21 4BG | CT (DFES) | 1.892 | 1.781 | 1.623 | 1.446 | 1.192 | 0.83 | 0.461 | 0.084 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER 33/11KV | 11 | 33 | Blucher | STELLA NORTH | NE15 9SB | CT (DFES) | 14.4552 | 14.3332 | 14.1732 | 13.9922 | 13.7282 | 13.3452 | 12.9572 | 12.5622 | 12.1272 | 11.6662 | 9.1752 | 6.6112 | 4.0452 | 1.5822 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOLDON DOWNHILL | 20 | 66 | West Boldon | WEST BOLDON | NE36 0AS | CT (DFES) | 19.2645 | 19.1685 | 19.0415 | 18.8995 | 18.6905 | 18.3885 | 18.0815 | 17.7705 | 17.4265 | 17.0625 | 15.0935 | 13.0705 | 11.0455 | 9.1005 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | YO51 9NS | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 33/11KV | 11 | 33 | Bowesfield | NORTON | TS18 3HR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 66/11KV | 11 | 66 | North Tees | NORTON | TS23 1PX | CT (DFES) | 39.2771 | 39.2081 | 39.1101 | 39.0001 | 38.8421 | 38.6181 | 38.3891 | 38.1551 | 37.8951 | 37.6161 | 36.0871 | 34.5891 | 33.0691 | 31.6061 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BRANCEPETH | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL15 0TW | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BREAMISH STREET | 11 | 66 | West Boldon | WEST BOLDON | NE1 2BL | CT (DFES) | 22.442 | 22.394 | 22.325 | 22.248 | 22.137 | 21.981 | 21.821 | 21.658 | 21.476 | 21.281 | 20.211 | 19.17 | 18.112 | 17.094 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BRENDA TRADING | 11 | 66 | Hartmoor | HARTMOOR | TS25 1PD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CAMPLESHON ROAD | 11 | 33 | Melrosegate | OSBALDWICK | YO23 1HZ | CT (DFES) | 0.3527 | 0.2277 | 0.055703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARLEY HILL | 11 | 66 | West Boldon | WEST BOLDON | SR5 1SG | CT (DFES) | 19.495 | 19.35 | 19.151 | 18.926 | 18.602 | 18.138 | 17.665 | 17.183 | 16.65 | 16.081 | 12.981 | 9.88 | 6.753 | 3.746 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARLIN HOW T3 T4 | 11 | 66 | Lackenby | LACKENBY | TS13 4DL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARR HILL | 11 | 66 | West Boldon | WEST BOLDON | NE10 9SY | CT (DFES) | 19.9169 | 19.7419 | 19.5069 | 19.2419 | 18.8569 | 18.3009 | 17.7369 | 17.1619 | 16.5279 | 15.8529 | 12.1949 | 8.4729 | 4.7349 | 1.1439 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CATTERICK CAMP | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL9 3HE | CT (DFES) | 8.532 | 8.337 | 8.067 | 7.763 | 7.323 | 6.69 | 6.036 | 5.355 | 4.588 | 3.755 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CLOSE | 11 | 66 | Dunston | STELLA NORTH | NE1 3NB | CT (DFES) | 12.76 | 12.721 | 12.651 | 12.571 | 12.465 | 12.322 | 12.174 | 12.02 | 11.846 | 11.652 | 10.553 | 9.621 | 8.633 | 7.678 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CONEYTHORPE | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG5 0RZ | CT (DFES) | 6.7936 | 6.7026 | 6.5746 | 6.4306 | 6.2246 | 5.9296 | 5.6266 | 5.3136 | 4.9656 | 4.5906 | 2.5336 | 0.49162 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CONSETT | 20 | 66 | Annfield | STELLA SOUTH | DH8 7ND | CT (DFES) | 7.638 | 7.436 | 7.155 | 6.839 | 6.384 | 5.732 | 5.065 | 4.38 | 3.618 | 2.799 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CORPORATION STREET | 11 | 33 | Barrack Road | STELLA NORTH | NE4 5SS | CT (DFES) | 19.5585 | 19.5225 | 19.4695 | 19.4105 | 19.3255 | 19.2055 | 19.0835 | 18.9585 | 18.8195 | 18.6695 | 17.8495 | 17.0525 | 16.2415 | 15.4615 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | COWTON | 11 | 33 | Darlington Central | NORTON | DL6 2NF | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLEY | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 2PP | CT (DFES) | 9.493 | 9.457 | 9.402 | 9.34 | 9.254 | 9.132 | 9.006 | 8.876 | 8.731 | 8.571 | 7.69 | 6.853 | 5.995 | 5.164 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 132/6KV | 6 | 132 | Darlington 132/6kV | NORTON | DL1 1SW | CT (DFES) | 0 | 29.6994 | 29.6194 | 29.5294 | 29.4014 | 29.2174 | 29.0294 | 28.8374 | 28.6244 | 28.3964 | 27.1484 | 25.9104 | 24.6584 | 23.4534 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1SW | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1HG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON EAST | 11 | 33 | Darlington Central | NORTON | DL1 4NP | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON WEST | 11 | 33 | Darlington North | NORTON | DL3 9QG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DENWICK | 20 | 66 | Linton | BLYTH 132kV | NE66 3RG | CT (DFES) | 5.835 | 5.638 | 5.343 | 5.01 | 4.54 | 3.879 | 3.193 | 2.478 | 1.672 | 0.788 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/11KV | 11 | 66 | Dunston | STELLA NORTH | NE11 9DH | CT (DFES) | 1.3293 | 1.2663 | 1.1743 | 1.0703 | 0.92228 | 0.71328 | 0.50028 | 0.28128 | 0.039278 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/20KV | 20 | 66 | Dunston | STELLA NORTH | NE11 9DH | CT (DFES) | 11.931 | 11.803 | 11.628 | 11.431 | 11.145 | 10.735 | 10.318 | 9.892 | 9.422 | 8.921 | 6.196 | 3.45 | 0.685 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DURHAM EAST | 11 | 66 | Potter House | SPENNYMOOR | DH1 5SU | CT (DFES) | 22.0908 | 22.0468 | 21.9718 | 21.8848 | 21.7688 | 21.6108 | 21.4458 | 21.2748 | 21.0818 | 20.8678 | 19.6618 | 18.5988 | 17.4848 | 16.4058 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EASTFIELD | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 3BY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.4169 | 19.9289 | 19.4079 | 16.5749 | 13.6749 | 10.7599 | 7.9499 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EASTGATE CEMENT | 20 | 66 | Toronto | SPENNYMOOR | DL13 2LA | CT (DFES) | 11.637 | 11.605 | 11.555 | 11.497 | 11.418 | 11.308 | 11.194 | 11.076 | 10.944 | 10.799 | 9.99 | 9.246 | 8.476 | 7.732 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | Barrack Road | STELLA NORTH | NE5 4JQ | CT (DFES) | 22.6809 | 22.6189 | 22.5309 | 22.4309 | 22.2889 | 22.0869 | 21.8809 | 21.6709 | 21.4369 | 21.1859 | 19.8059 | 18.4659 | 17.1029 | 15.7909 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ELVINGTON | 11 | 33 | Melrosegate | OSBALDWICK | YO41 4DY | CT (DFES) | 0.9337 | 0.9077 | 0.8697 | 0.8257 | 0.7647 | 0.6797 | 0.5917 | 0.5007 | 0.3997 | 0.2887 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FARADAY STREET | 11 | 66 | North Tees | NORTON | TS1 4JG | CT (DFES) | 13.1248 | 12.9778 | 12.7688 | 12.5328 | 12.1958 | 11.7168 | 11.2268 | 10.7278 | 10.1738 | 9.5788 | 6.3258 | 3.1358 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | Blyth 66kV | BLYTH 66KV | NE3 2SW and NE13 6BH | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FISHBURN | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | TS29 6JQ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH CENTRAL | 11 | 33 | Flatworth | TYNEMOUTH | NE29 7SH | CT (DFES) | 30.6507 | 30.5857 | 30.4957 | 30.3937 | 30.2467 | 30.0377 | 29.8237 | 29.6067 | 29.3657 | 29.1077 | 27.7027 | 26.3057 | 24.8947 | 23.5377 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FOSS ISLANDS | 11 | 33 | Melrosegate | OSBALDWICK | YO31 7US | CT (DFES) | 1.2907 | 1.1537 | 0.9537 | 0.7287 | 0.4087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FOSSWAY 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE6 4AN | CT (DFES) | 14.3109 | 14.1729 | 13.9849 | 13.7729 | 13.4669 | 13.0259 | 12.5769 | 12.1209 | 11.6159 | 11.0779 | 8.1569 | 5.2119 | 2.2459 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FYLANDS BRIDGE | 11 | 66 | Toronto | SPENNYMOOR | DL14 9TA | CT (DFES) | 9.886 | 9.727 | 9.508 | 9.261 | 8.905 | 8.393 | 7.869 | 7.332 | 6.737 | 6.098 | 2.616 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GALE LANE | 11 | 33 | Poppleton | POPPLETON | YO24 3AF | CT (DFES) | 7.692 | 7.562 | 7.39 | 7.198 | 6.915 | 6.505 | 6.089 | 5.665 | 5.198 | 4.704 | 2.033 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GARWOOD STREET | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 5DQ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.0106 | 19.5836 | 19.1216 | 16.5886 | 14.1426 | 11.6506 | 9.2516 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD CENTRAL | 11 | 33 | Barrack Road | STELLA NORTH | NE8 1HB | CT (DFES) | 16.8948 | 16.8478 | 16.7748 | 16.6918 | 16.5768 | 16.4168 | 16.2518 | 16.0828 | 15.8938 | 15.6878 | 14.5478 | 13.4848 | 12.3908 | 11.3358 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD EAST | 11 | 66 | West Boldon | WEST BOLDON | NE8 3AH | CT (DFES) | 22.618 | 22.612 | 22.6 | 22.588 | 22.57 | 22.546 | 22.522 | 22.496 | 22.467 | 22.436 | 22.259 | 22.102 | 21.937 | 21.779 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE3 1RR | CT (DFES) | 30.48 | 30.431 | 30.361 | 30.283 | 30.171 | 30.012 | 29.849 | 29.683 | 29.499 | 29.301 | 28.223 | 27.159 | 26.082 | 25.046 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GRANGETOWN | 11 | 66 | Lackenby | LACKENBY | TS6 7AS | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GREATHAM | 11 | 132 | Greatham | SALTHOLME | TS25 2DD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | Lackenby | LACKENBY | TS14 6GQ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARLOW GREEN | 11 | 66 | West Boldon | WEST BOLDON | NE9 6NT | CT (DFES) | 14.3541 | 14.2021 | 13.9981 | 13.7691 | 13.4351 | 12.9541 | 12.4641 | 11.9661 | 11.4161 | 10.8311 | 7.6621 | 4.4351 | 1.1951 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARMIRE BRIDGE | 20 | 66 | Toronto | SPENNYMOOR | DL12 8QJ | CT (DFES) | 8.29 | 8.196 | 8.051 | 7.886 | 7.657 | 7.338 | 7.007 | 6.665 | 6.282 | 5.862 | 3.532 | 1.35 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARRATON | 11 | 132 | Harraton | STELLA SOUTH | NE38 9BZ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.2 | 35.852 | 35.478 | 33.428 | 31.424 | 29.389 | 27.432 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/11KV | 11 | 132 | Harrogate 132/11kV | KNARESBOROUGH | HG1 2BN | CT (DFES) | 27.533 | 27.283 | 26.933 | 26.539 | 25.972 | 25.163 | 24.332 | 23.476 | 22.521 | 21.491 | 15.846 | 10.247 | 4.57 | -0.911 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE WEST | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 0QB | CT (DFES) | 32.553 | 32.492 | 32.403 | 32.302 | 32.16 | 31.957 | 31.749 | 31.534 | 31.294 | 31.033 | 29.599 | 28.203 | 26.781 | 25.406 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARTMOOR 66/20KV | 20 | 66 | Hartmoor | HARTMOOR | TS27 3BL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HAWTHORN PIT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 9NX | CT (DFES) | 10.337 | 10.129 | 9.846 | 9.527 | 9.065 | 8.4 | 7.722 | 7.03 | 6.262 | 5.441 | 0.975 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | Melrosegate | OSBALDWICK | YO31 8FZ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN | 6 | 66 | West Boldon | WEST BOLDON | NE31 1BD | CT (DFES) | 0 | 4.8428 | 4.8058 | 4.7638 | 4.7048 | 4.6208 | 4.5348 | 4.4468 | 4.3498 | 4.2448 | 3.6708 | 3.1108 | 2.5418 | 1.9938 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN WEST | 11 | 66 | West Boldon | WEST BOLDON | NE31 1NA | CT (DFES) | 0.0016837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEDWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE32 4SW | CT (DFES) | 0.33529 | 0.24429 | 0.12229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEIGHINGTON | 11 | 33 | Darlington North | NORTON | DL5 6JW | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEXHAM | 20 | 66 | Coalburns | STELLA SOUTH | NE46 4NT | CT (DFES) | 27.9649 | 27.8649 | 27.7219 | 27.5599 | 27.3299 | 27.0009 | 26.6619 | 26.3089 | 25.9119 | 25.4799 | 23.0979 | 20.7589 | 18.3749 | 16.0649 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HIGH BARMSTON | 11 | 66 | West Boldon | WEST BOLDON | NE38 8QA | CT (DFES) | 20.704 | 20.608 | 20.474 | 20.323 | 20.107 | 19.797 | 19.482 | 19.16 | 18.804 | 18.423 | 16.34 | 14.278 | 12.192 | 10.187 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HIGH FLATTS | 11 | 66 | Potter House | SPENNYMOOR | DH2 2LR | CT (DFES) | 21.2852 | 21.1292 | 20.9152 | 20.6732 | 20.3242 | 19.8222 | 19.3092 | 18.7842 | 18.2002 | 17.5752 | 14.1642 | 10.7362 | 7.2772 | 3.9452 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HOUGHTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | DH4 5HP | CT (DFES) | 3.7591 | 3.6261 | 3.4441 | 3.2391 | 2.9431 | 2.5171 | 2.0821 | 1.6381 | 1.1471 | 0.62314 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HOWDON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 0JX | CT (DFES) | 4.3325 | 4.2955 | 4.2465 | 4.1915 | 4.1115 | 3.9955 | 3.8785 | 3.7585 | 3.6265 | 3.4865 | 2.7245 | 1.9525 | 1.1765 | 0.43151 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUNTINGTON NEW LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO32 9TA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | Husthwaite | KNARESBOROUGH | YO61 4PN | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | JARROW | 11 | 33 | South Shields | SOUTH SHIELDS | NE32 5LD | CT (DFES) | 18.4056 | 18.3766 | 18.3366 | 18.2906 | 18.2256 | 18.1326 | 18.0376 | 17.9406 | 17.8336 | 17.7186 | 17.0896 | 16.4706 | 15.8436 | 15.2406 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KENTON | 11 | 33 | Blucher | STELLA NORTH | NE3 4UP | CT (DFES) | 3.1571 | 3.0561 | 2.9231 | 2.7731 | 2.5541 | 2.2371 | 1.9151 | 1.5881 | 1.2281 | 0.8451 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KIELDER | 20 | 33 | Spadeadam 33kV | SPADEADAM | NE48 1BH | CT (DFES) | 4.052 | 4.045 | 4.032 | 4.017 | 3.997 | 3.97 | 3.942 | 3.912 | 3.878 | 3.84 | 3.627 | 3.437 | 3.238 | 3.044 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KILLINGWORTH | 11 | 33 | Gosforth | TYNEMOUTH | NE12 6QQ | CT (DFES) | 11.552 | 11.461 | 11.339 | 11.202 | 11.002 | 10.713 | 10.42 | 10.122 | 9.794 | 9.444 | 7.554 | 5.624 | 3.688 | 1.829 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KIRBYMOORSIDE | 11 | 66 | Malton Grid | OSBALDWICK | YO62 6EZ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LINTON 66/20KV | 20 | 66 | Linton | BLYTH 132kV | NE61 3AX | CT (DFES) | 7.338 | 7.25 | 7.128 | 6.99 | 6.792 | 6.507 | 6.213 | 5.908 | 5.566 | 5.195 | 3.16 | 1.123 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LONGBENTON | 11 | 33 | Gosforth | TYNEMOUTH | NE7 7LR | CT (DFES) | 19.5262 | 19.4092 | 19.2532 | 19.0782 | 18.8222 | 18.4522 | 18.0762 | 17.6942 | 17.2732 | 16.8262 | 14.4062 | 11.9302 | 9.4482 | 7.0642 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LOW SPENNYMOOR | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL16 7RS | CT (DFES) | 7.977 | 7.882 | 7.753 | 7.608 | 7.398 | 7.096 | 6.787 | 6.47 | 6.119 | 5.743 | 3.695 | 1.626 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LYNEMOUTH | 20 | 66 | Linton | BLYTH 132kV | NE61 5XH | CT (DFES) | 6.066 | 6.043 | 6.013 | 5.978 | 5.928 | 5.855 | 5.78 | 5.702 | 5.615 | 5.521 | 5.009 | 4.487 | 3.96 | 3.45 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MADDISON STREET | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE24 1HD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALLEABLE | 11 | 66 | North Tees | NORTON | TS18 2NR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0899 | 0.77488 | 0.43188 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALTON | 11 | 66 | Malton Grid | OSBALDWICK | YO17 6BT | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MEADOWFIELD | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH7 8ER | CT (DFES) | 0.88 | 0.834 | 0.768 | 0.692 | 0.585 | 0.435 | 0.28 | 0.12 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 33/11KV | 11 | 33 | Melrosegate | OSBALDWICK | YO31 0YB | CT (DFES) | 1.6377 | 1.5627 | 1.4607 | 1.3457 | 1.1787 | 0.9397 | 0.6957 | 0.4477 | 0.1727 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MILLBANK LANE | 11 | 33 | Bowesfield | NORTON | TS17 0AX | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1292 | 17.6522 | 17.1452 | 14.3942 | 11.5932 | 8.7812 | 6.0782 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MONKSEATON | 11 | 33 | Chirton Grange | TYNEMOUTH | NE25 9AF | CT (DFES) | 19.3582 | 19.1852 | 18.9492 | 18.6832 | 18.2982 | 17.7442 | 36.418 | 35.841 | 35.202 | 34.518 | 30.801 | 27.05 | 23.272 | 19.636 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MOOR MONKTON PUMPS | 11 | 33 | Poppleton | POPPLETON | YO30 1BY | CT (DFES) | 13.4029 | 13.3869 | 13.3639 | 13.3379 | 13.3019 | 13.2489 | 13.1949 | 13.1389 | 13.0769 | 13.0089 | 12.6389 | 12.2729 | 11.9009 | 11.5419 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MORPETH | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE61 6JH | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MOUNT ROAD | 11 | 33 | Offerton | OFFERTON | SR4 7LJ | CT (DFES) | 24.0412 | 23.9112 | 23.7262 | 23.5172 | 23.2192 | 22.7962 | 22.3642 | 21.9222 | 21.4322 | 20.9062 | 18.0252 | 15.2052 | 12.3432 | 9.5892 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWBURN HAUGH | 11 | 132 | Newburn Haugh | STELLA NORTH | NE15 8SF | CT (DFES) | 20.4324 | 20.3894 | 20.3324 | 20.2674 | 20.1734 | 20.0384 | 19.9014 | 19.7614 | 19.6064 | 19.4424 | 18.5504 | 17.6464 | 16.7374 | 15.8644 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWBY | 11 | 33 | Scarborough Grid | OSBALDWICK | YO12 6NL | CT (DFES) | 0.16187 | 0.046868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWCASTLE AIRPORT | 11 | 33 | Blucher | STELLA NORTH | NE13 8DF | CT (DFES) | 27.0983 | 27.0163 | 26.9063 | 26.7823 | 26.6013 | 26.3403 | 26.0733 | 25.7983 | 25.4933 | 25.1663 | 23.3863 | 21.5703 | 19.7433 | 17.9803 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | Darlington North | NORTON | DL5 6EA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH STREET | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 1DU | CT (DFES) | 1.3834 | 1.2994 | 1.1734 | 1.0314 | 0.8314 | 0.5504 | 0.2594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T1 T2 | 11 | 66 | North Tees | NORTON | TS23 1PX | CT (DFES) | 22.3424 | 22.3244 | 22.2824 | 22.2334 | 22.1724 | 22.0954 | 22.0134 | 21.9264 | 21.8274 | 21.7114 | 21.0384 | 20.5434 | 19.9954 | 19.4604 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T3 T4 | 11 | 66 | North Tees | NORTON | TS23 1PY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1487 | 7.9067 | 7.6407 | 6.1647 | 4.8157 | 3.4187 | 2.0707 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTHALLERTON | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 0QE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTON 132/11KV | 11 | 132 | Norton 132/11kV | NORTON | TS21 1EG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | OATLANDS | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 8BY | CT (DFES) | 18.2608 | 18.1658 | 18.0348 | 17.8868 | 17.6738 | 17.3668 | 17.0528 | 16.7298 | 16.3708 | 15.9838 | 13.8718 | 11.7478 | 9.6018 | 7.5318 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | OFFERTON 33/11KV | 11 | 33 | Offerton | OFFERTON | SR4 9NR | CT (DFES) | 26.5308 | 26.3848 | 26.1908 | 25.9728 | 25.6548 | 25.1958 | 24.7278 | 24.2528 | 23.7288 | 23.1718 | 20.1578 | 17.0718 | 13.9778 | 11.0058 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PALLION TRADING | 11 | 33 | Offerton | OFFERTON | SR4 6SN | CT (DFES) | 13.5668 | 13.4538 | 13.2958 | 13.1168 | 12.8618 | 12.4968 | 12.1238 | 11.7438 | 11.3238 | 10.8728 | 8.4108 | 5.9768 | 3.5128 | 1.1438 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2HR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE WEST | 11 | 66 | Hartmoor | HARTMOOR | DH6 2RA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PILGRIM | 11 | 33 | Barrack Road | STELLA NORTH | NE1 2LA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7042 | 3.6442 | 3.5732 | 3.1672 | 2.8622 | 2.5252 | 2.1982 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | Potter House | SPENNYMOOR | DH1 5FF | CT (DFES) | 4.445 | 4.27 | 4.033 | 3.767 | 3.379 | 2.821 | 2.251 | 1.667 | 1.02 | 0.32705 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | Potter House | SPENNYMOOR | DH1 5FF | CT (DFES) | 26.2222 | 26.1992 | 26.1632 | 26.1232 | 26.0672 | 25.9892 | 25.9082 | 25.8242 | 25.7312 | 25.6302 | 25.0672 | 24.5352 | 23.9882 | 23.4602 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PRISSICK | 11 | 66 | Lackenby | LACKENBY | TS4 3SG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSCAR | 11 | 33 | Scarborough Grid | OSBALDWICK | YO13 0LZ | CT (DFES) | 10.019 | 10.009 | 9.994 | 9.977 | 9.953 | 9.919 | 9.884 | 9.848 | 9.807 | 9.763 | 9.521 | 9.288 | 9.05 | 8.819 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAWCLIFFE LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO30 5SW | CT (DFES) | 0.8147 | 0.7057 | 0.5557 | 0.3867 | 0.1427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | REDCAR | 11 | 66 | Lackenby | LACKENBY | TS10 2PA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RESERVOIR | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE22 5QP | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T1 | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL10 5BJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T2 | 11 | 33 | Darlington North | NORTON | DL10 5BJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RIPON | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG4 1QE | CT (DFES) | 14.3339 | 14.1769 | 13.9509 | 17.653 | 17.291 | 16.775 | 16.246 | 15.699 | 15.088 | 14.426 | 10.783 | 7.228 | 3.608 | 0.11 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RISE CARR | 6 | 33 | Darlington North | NORTON | DL3 0RP | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ROMANBY | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 8HP | CT (DFES) | 9.9401 | 9.8611 | 9.7571 | 9.6411 | 9.4701 | 9.2221 | 8.9681 | 8.7071 | 8.4161 | 8.1051 | 6.4141 | 4.6681 | 2.9171 | 1.2261 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RUDBY | 11 | 33 | Bowesfield | NORTON | TS15 0JT | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 2YH | CT (DFES) | 2.129 | 1.975 | 1.76 | 1.519 | 1.17 | 0.67102 | 0.16002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEGHILL | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 7EY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | Husthwaite | KNARESBOROUGH | YO7 3NT | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEVERUS HILL | 11 | 33 | Poppleton | POPPLETON | YO26 4RR | CT (DFES) | 0.72957 | 0.62657 | 0.48557 | 0.32757 | 0.098571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SHERIFF HUTTON | 11 | 66 | Malton Grid | OSBALDWICK | YO60 6QN | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SHOTTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2EL | CT (DFES) | 1.3132 | 1.2082 | 1.0632 | 0.89917 | 0.66217 | 0.32317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SIMONSIDE | 11 | 33 | South Shields | SOUTH SHIELDS | NE34 9PD | CT (DFES) | 13.1741 | 13.0891 | 12.9731 | 12.8441 | 12.6561 | 12.3851 | 12.1101 | 11.8301 | 11.5211 | 11.1921 | 9.4051 | 7.5971 | 5.7781 | 4.0321 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SKELDERGATE | 11 | 33 | Poppleton | POPPLETON | YO1 6HN | CT (DFES) | 2.0929 | 2.0469 | 1.9749 | 1.8919 | 1.7779 | 1.6209 | 1.4589 | 1.2909 | 1.1039 | 0.89888 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SKERNESIDE | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL5 6JH | CT (DFES) | 0.24062 | 0.11362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENCERBECK | 11 | 66 | Lackenby | LACKENBY | TS3 8TE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5JX | CT (DFES) | 0.67067 | 0.53567 | 0.34867 | 0.13767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STARBECK | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 7PT | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STOKESLEY | 11 | 33 | Bowesfield | NORTON | TS9 5HS | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STONEY CUT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 8RQ | CT (DFES) | 15.8242 | 15.6882 | 15.5022 | 15.2922 | 14.9892 | 14.5532 | 14.1082 | 13.6512 | 13.1452 | 12.6012 | 9.6392 | 6.6602 | 3.6542 | 0.75725 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T1 T2 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | CT (DFES) | 20.9993 | 20.9163 | 20.7843 | 20.6323 | 20.4253 | 20.1393 | 19.8453 | 19.5403 | 19.2013 | 18.8283 | 16.7483 | 14.8613 | 12.9043 | 11.0153 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T5 T6 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | CT (DFES) | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.799 | 22.799 | 22.799 | 22.799 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TANFIELD | 11 | 66 | Annfield | STELLA SOUTH | DH9 9DB | CT (DFES) | 0.54015 | 0.41315 | 0.23915 | 0.04415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEAM VALLEY | 20 | 66 | Ravensworth | STELLA SOUTH | NE11 0SX | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.9411 | 44.8061 | 44.6531 | 43.7831 | 43.0701 | 42.3071 | 41.5671 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | Seal Sands | SALTHOLME | TS23 3NF | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEMPLE PARK | 11 | 66 | West Boldon | WEST BOLDON | NE34 8TH | CT (DFES) | 20.0124 | 19.8644 | 19.6674 | 19.4474 | 19.1244 | 18.6574 | 18.1844 | 17.7024 | 17.1714 | 16.6084 | 13.5624 | 10.4384 | 7.3084 | 4.3034 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | THIRSK | 11 | 33 | Leeming Bar_Skeeby | NORTON | YO7 4NH | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | THORNTON DALE | 11 | 66 | Malton Grid | OSBALDWICK | YO18 7SJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO 66/20KV | 20 | 66 | Toronto | SPENNYMOOR | DL14 7RJ | CT (DFES) | 8.095 | 7.945 | 7.73 | 7.486 | 7.141 | 6.65 | 6.146 | 5.628 | 5.051 | 4.427 | 1 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TUNSTALL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR3 2BT | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5469 | 23.9159 | 23.2459 | 19.6169 | 15.9059 | 12.1849 | 8.6119 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE30 1JG | CT (DFES) | 19.6535 | 19.5205 | 19.3335 | 19.1215 | 18.8185 | 18.3875 | 17.9475 | 17.4985 | 17.0015 | 16.4675 | 13.5525 | 10.6785 | 7.7685 | 4.9695 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | UNIVERSITY | 11 | 33 | Barrack Road | STELLA NORTH | NE2 4PZ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3817 | 10.2797 | 10.1677 | 9.5457 | 8.9697 | 8.3757 | 7.8037 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | URLAY NOOK | 11 | 33 | Bowesfield | NORTON | TS16 0QB | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | USWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE37 3HY | CT (DFES) | 21.59 | 21.533 | 21.453 | 21.364 | 21.235 | 21.051 | 20.863 | 20.671 | 20.46 | 20.233 | 19.003 | 17.77 | 16.527 | 15.332 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WALKER | 11 | 66 | West Boldon | WEST BOLDON | NE6 3PZ | CT (DFES) | 14.5649 | 14.4389 | 14.2689 | 14.0779 | 13.8009 | 13.4009 | 12.9949 | 12.5819 | 12.1259 | 11.6399 | 9.0049 | 6.3339 | 3.6489 | 1.0699 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WANSBECK | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE22 7DH | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WARDLEY | 6 | 66 | West Boldon | WEST BOLDON | NE31 1LP | CT (DFES) | 0 | 15.6674 | 15.5724 | 15.4654 | 15.3094 | 15.0864 | 14.8594 | 14.6274 | 14.3724 | 14.1004 | 12.6224 | 11.1274 | 9.6234 | 8.1794 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WARKWORTH | 20 | 66 | Linton | BLYTH 132kV | NE65 0YD | CT (DFES) | 6.346 | 6.182 | 5.946 | 5.68 | 5.301 | 4.761 | 4.202 | 3.622 | 2.969 | 2.257 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WENSLEYDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5ED | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST HARTFORD | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 3JP | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST SOUTHWICK | 11 | 66 | West Boldon | WEST BOLDON | SR5 3TX | CT (DFES) | 20.618 | 20.546 | 20.447 | 20.335 | 20.173 | 19.941 | 19.705 | 19.464 | 19.198 | 18.914 | 17.37 | 15.821 | 14.259 | 12.758 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST WYLAM | 20 | 66 | Coalburns | STELLA SOUTH | NE42 5EX | CT (DFES) | 0.13436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WESTERHOPE | 11 | 33 | Blucher | STELLA NORTH | NE5 5HH | CT (DFES) | 19.0123 | 18.9023 | 18.7563 | 18.5933 | 18.3543 | 18.0073 | 17.6553 | 17.2983 | 16.9043 | 16.4863 | 14.2333 | 11.9093 | 9.5843 | 7.3523 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WESTOE | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 3GE | CT (DFES) | 13.124 | 13.012 | 12.86 | 12.688 | 12.44 | 12.083 | 11.72 | 11.351 | 10.943 | 10.508 | 8.146 | 5.761 | 3.362 | 1.056 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO22 4JE | CT (DFES) | 11.7801 | 11.7511 | 11.7091 | 11.6611 | 11.5941 | 11.4981 | 11.4001 | 11.2991 | 11.1851 | 11.0621 | 10.3871 | 9.7281 | 9.0571 | 8.4091 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO22 4JE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO21 1LY | CT (DFES) | 11.6979 | 11.6599 | 11.6059 | 11.5469 | 11.4599 | 11.3359 | 11.2089 | 11.0789 | 10.9329 | 10.7759 | 9.9189 | 9.0629 | 8.1959 | 7.3599 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO21 1LY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WILLINGTON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 7HS | CT (DFES) | 18.4982 | 18.3802 | 18.2232 | 18.0472 | 17.7892 | 17.4162 | 17.0372 | 16.6532 | 16.2292 | 15.7802 | 13.3522 | 10.8532 | 8.3522 | 5.9512 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | Wormald Green 132/11kV | KNARESBOROUGH | HG3 3PS | CT (DFES) | 13.111 | 13.035 | 12.928 | 12.807 | 12.633 | 12.386 | 12.132 | 11.871 | 11.579 | 11.263 | 9.532 | 7.824 | 6.089 | 4.414 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WYNYARD | 11 | 66 | Hartmoor | HARTMOOR | TS2 2FB | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | YEDINGHAM | 11 | 66 | Malton Grid | OSBALDWICK | YO17 8RR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | YORK UNIVERSITY | 11 | 33 | Melrosegate | OSBALDWICK | YO10 5ZF | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ABBEY ROAD | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS5 3NF | CT (DFES) | 1.8233 | 1.7523 | 1.6613 | 1.5593 | 1.4113 | 1.1943 | 0.97333 | 0.74733 | 0.49733 | 0.23133 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AIREDALE ROAD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 4LJ | CT (DFES) | 13.0496 | 12.9966 | 12.9296 | 12.8546 | 12.7436 | 12.5816 | 12.4176 | 12.2486 | 12.0626 | 11.8646 | 10.7886 | 9.6376 | 8.4716 | 7.3316 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALDHAM | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S73 8SW | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALFRED GELDER STREET | 11 | 33 | Hull South | CREYKE BECK | HU1 1EP | CT (DFES) | 2.8609 | 2.8329 | 2.7959 | 2.7559 | 2.6949 | 2.6079 | 2.5179 | 2.4279 | 2.3279 | 2.2219 | 1.6479 | 1.0319 | 0.40985 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T1 | 11 | 33 | Leeds East | SKELTON GRANGE | LS7 3QB | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T2 | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 3QB | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALVERTHORPE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 9PB | CT (DFES) | 21.6143 | 21.4853 | 21.3183 | 21.1313 | 20.8623 | 20.4743 | 20.0763 | 19.6683 | 19.2143 | 18.7273 | 16.0573 | 13.2923 | 10.4683 | 7.7053 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARMOURIES DRIVE | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LT | CT (DFES) | 7.094 | 7.061 | 7.019 | 6.971 | 6.902 | 6.8 | 6.697 | 6.591 | 6.474 | 6.35 | 5.672 | 4.951 | 4.221 | 3.506 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARMTHORPE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3DY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARUNDEL STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4PJ | CT (DFES) | 4.4238 | 4.4058 | 4.3828 | 4.3578 | 4.3198 | 4.2638 | 4.2078 | 4.1508 | 4.0868 | 4.0188 | 3.6518 | 3.2578 | 2.8598 | 2.4708 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ASKERN | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN6 0BY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AUDBY LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 7SU | CT (DFES) | 3.5154 | 3.4184 | 3.2914 | 3.1484 | 2.9484 | 2.6644 | 2.3704 | 2.0664 | 1.7254 | 1.3544 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AUSTERFIELD | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN10 6HD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BAILIFF BRIDGE | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 4DT | CT (DFES) | 1.2615 | 1.1875 | 1.0935 | 0.98848 | 0.83548 | 0.61248 | 0.38348 | 0.14748 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BALBY | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN4 8DG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BALME STREET | 11 | 33 | Bradford | BRADFORD WEST | BD1 4BA | CT (DFES) | 3.2926 | 3.2406 | 3.1736 | 3.0986 | 2.9896 | 2.8296 | 2.6666 | 2.5006 | 2.3156 | 2.1206 | 1.0566 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNBURGH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 9NT | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNOLDSWICK | 11 | 33 | Silsden | BRADFORD WEST | BB18 5RU | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 7AU | CT (DFES) | 32.1312 | 32.0802 | 32.0142 | 31.9412 | 31.8332 | 31.6762 | 31.5162 | 31.3522 | 31.1712 | 30.9792 | 29.9342 | 28.8142 | 27.6812 | 26.5742 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARROW | 11 | 33 | Immingham | GRIMSBY WEST | DN19 7EG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 66/11KV | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1HT | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARWICK | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS15 8SW | CT (DFES) | 13.0614 | 12.9674 | 12.8484 | 12.7144 | 12.5184 | 12.2334 | 11.9424 | 11.6444 | 11.3144 | 10.9644 | 9.0544 | 7.0254 | 4.9664 | 2.9544 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BASLOW ROAD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S17 3LT | CT (DFES) | 0.18592 | 0.10692 | 0.0069191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BATLEY | 11 | 33 | Thornhill 132kV | ELLAND | WF17 6HU | CT (DFES) | 4.7894 | 4.6604 | 4.4964 | 4.3124 | 4.0444 | 3.6534 | 3.2534 | 2.8444 | 2.3904 | 1.9074 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEAL | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8DT | CT (DFES) | 3.8781 | 3.8221 | 3.7491 | 3.6671 | 3.5541 | 3.3921 | 3.2231 | 3.0451 | 2.8431 | 2.6221 | 1.3901 | 0.14707 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | CT (DFES) | 8.5595 | 8.5315 | 8.4955 | 8.4555 | 8.3975 | 8.3115 | 8.2245 | 8.1355 | 8.0375 | 7.9325 | 7.3615 | 6.7555 | 6.1405 | 5.5385 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | CT (DFES) | 38.3902 | 38.3242 | 38.2392 | 38.1442 | 38.0062 | 37.8042 | 37.5982 | 37.3872 | 37.1542 | 36.9062 | 35.5552 | 34.1182 | 32.6612 | 31.2372 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEIGHTON | 11 | 66 | Thurcroft | THURCROFT | S26 4TL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELLHOUSE ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 0PL | CT (DFES) | 1.2597 | 1.1327 | 0.97173 | 0.79073 | 0.52573 | 0.13873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT AVENUE | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DF | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT COVERT | 11 | 33 | Wold Newton | KEADBY | LN11 9RA | CT (DFES) | 0.021462 | 0.012462 | 0.00046236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELTHORPE LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1SB | CT (DFES) | 12.328 | 12.31 | 12.286 | 12.26 | 12.224 | 12.173 | 12.119 | 12.062 | 11.997 | 11.924 | 11.52 | 11.118 | 10.701 | 10.288 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BENTLEY | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN5 0NG | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BILLET LANE | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINBROOK | 11 | 33 | Wold Newton | KEADBY | LN8 6DR | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 33/11KV | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | CT (DFES) | 13.3536 | 13.2586 | 13.1366 | 13.0006 | 12.8006 | 12.5096 | 12.2116 | 11.9076 | 11.5706 | 11.2136 | 9.2666 | 7.1866 | 5.0796 | 3.0196 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BIRKBY | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 5HB | CT (DFES) | 0.22855 | 0.12955 | 0.0035485 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1HF | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLUE BOY STREET | 11 | 33 | Neepsend | NEEPSEND | S3 7BA | CT (DFES) | 1.349 | 1.33 | 1.305 | 1.276 | 1.235 | 1.175 | 1.113 | 1.051 | 0.98096 | 0.90696 | 0.50596 | 0.076961 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOC BRINSWORTH | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1WT | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOLTON ROAD | 11 | 33 | Silsden | BRADFORD WEST | BD20 0JT | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOTTESFORD | 11 | 33 | Scunthorpe South | KEADBY | DN16 3UJ | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHOPE | 11 | 33 | Menston | BRADFORD WEST | LS16 9HA | CT (DFES) | 0.74011 | 0.71611 | 0.68711 | 0.65311 | 0.60511 | 0.53411 | 0.46111 | 0.38711 | 0.30511 | 0.21811 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMLEY | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS13 3ST | CT (DFES) | 21.5648 | 21.4358 | 21.2698 | 21.0848 | 20.8138 | 20.4198 | 20.0178 | 19.6068 | 19.1508 | 18.6668 | 16.0278 | 13.2238 | 10.3778 | 7.5978 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRETT STREET | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 4HW | CT (DFES) | 17.0335 | 16.8015 | 16.5035 | 16.1695 | 15.7135 | 15.0585 | 14.3725 | 13.6445 | 12.8135 | 11.8995 | 6.7995 | 1.6425 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIDGES ROAD | 11 | 33 | Scunthorpe South | KEADBY | DN17 1HA | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1QE | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRODSWORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 7XB | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BROOKFIELD STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LD | CT (DFES) | 2.5349 | 2.5309 | 2.5269 | 2.5219 | 2.5149 | 2.5039 | 2.4939 | 2.4829 | 2.4709 | 2.4579 | 2.3879 | 2.3139 | 2.2389 | 2.1649 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BTP | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN31 2RL | CT (DFES) | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3827 | 16.3827 | 16.3827 | 16.3817 | 16.3797 | 16.3777 | 16.3757 | 16.3727 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURLEY STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS3 1JY | CT (DFES) | 39.9771 | 39.9401 | 39.8931 | 39.8391 | 39.7621 | 39.6491 | 39.5331 | 39.4151 | 39.2841 | 39.1451 | 38.3881 | 37.5831 | 36.7671 | 35.9691 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURMANTOFTS | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 7SS | CT (DFES) | 10.3005 | 10.2715 | 10.2335 | 10.1915 | 10.1305 | 10.0405 | 9.9495 | 9.8555 | 9.7525 | 9.6425 | 9.0425 | 8.4055 | 7.7585 | 7.1265 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURNLEYVILLE | 11 | 33 | Heckmondwike | SKELTON GRANGE | BD19 4RY | CT (DFES) | 1.8254 | 1.7244 | 1.5954 | 1.4514 | 1.2414 | 0.9354 | 0.6214 | 0.3014 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURTON PIDSEA | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU12 9AE | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURTON ROAD | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 2QG | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 2HG | CT (DFES) | 10.7673 | 10.6753 | 10.5583 | 10.4273 | 10.2363 | 9.9573 | 9.6723 | 9.3803 | 9.0583 | 8.7153 | 6.8473 | 4.8613 | 2.8463 | 0.87734 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BUTTERWICK | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO17 8HF | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CAISTOR | 11 | 33 | Wold Newton | KEADBY | LN7 6RE | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CALDER WHARF | 11 | 33 | Thornhill 132kV | ELLAND | WF13 3JQ | CT (DFES) | 19.8508 | 19.7428 | 19.6048 | 19.4498 | 19.2238 | 18.8958 | 18.5598 | 18.2158 | 17.8348 | 17.4288 | 15.2158 | 12.8618 | 10.4728 | 8.1368 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CARLTON HILL | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 1JB | CT (DFES) | 22.1924 | 22.1514 | 22.1004 | 22.0424 | 21.9584 | 21.8354 | 21.7104 | 21.5824 | 21.4404 | 21.2904 | 20.4684 | 19.5964 | 18.7104 | 17.8454 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CARR LANE | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 4PS | CT (DFES) | 22.4177 | 22.3317 | 22.2207 | 22.0967 | 21.9177 | 21.6587 | 21.3947 | 21.1227 | 20.8207 | 20.4967 | 18.7207 | 16.8807 | 15.0017 | 13.1637 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CHELKER RESERVOIR | 11 | 33 | Silsden | BRADFORD WEST | LS29 0JS | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CHEVIN END | 11 | 33 | Menston | BRADFORD WEST | LS29 6BE | CT (DFES) | 23.3815 | 23.3185 | 23.2375 | 23.1475 | 23.0155 | 22.8225 | 22.6255 | 22.4235 | 22.2015 | 21.9645 | 20.6775 | 19.3025 | 17.9085 | 16.5475 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENCE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1JE | CT (DFES) | 7.623 | 7.601 | 7.572 | 7.539 | 7.492 | 7.423 | 7.352 | 7.28 | 7.2 | 7.115 | 6.653 | 6.161 | 5.662 | 5.175 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON ROAD | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS2 9JT | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON STREET | 11 | 33 | Hull South | CREYKE BECK | HU3 1AP | CT (DFES) | 22.2529 | 22.2009 | 22.1339 | 22.0599 | 21.9489 | 21.7879 | 21.6249 | 21.4579 | 21.2749 | 21.0809 | 20.0279 | 18.8989 | 17.7569 | 16.6429 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLAYWHEELS LANE | 11 | 33 | Neepsend | NEEPSEND | S6 1LY | CT (DFES) | 22.5531 | 22.3871 | 22.1751 | 21.9381 | 21.5901 | 21.0821 | 20.5641 | 20.0351 | 19.4491 | 18.8281 | 15.4481 | 11.8301 | 8.1661 | 4.5871 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLOUGH LANE | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3EH | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COMMONSIDE LANE | 11 | 33 | Featherstone | FERRYBRIDGE B | WF7 5DF | CT (DFES) | 5.3208 | 5.2438 | 5.1448 | 5.7338 | 5.5728 | 5.3418 | 5.1058 | 4.8618 | 4.5918 | 4.3018 | 2.7118 | 1.0658 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CONVAMORE ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN32 9PG | CT (DFES) | 14.0193 | 13.9323 | 13.8213 | 13.6953 | 13.5143 | 13.2533 | 12.9853 | 12.7103 | 12.4043 | 12.0783 | 10.2873 | 8.4183 | 6.5143 | 4.6503 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CONYARD ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN35 7LQ | CT (DFES) | 10.6766 | 10.5606 | 10.4126 | 10.2456 | 10.0036 | 9.6556 | 9.2986 | 8.9316 | 8.5246 | 8.0886 | 5.7006 | 3.2096 | 0.66956 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CORNWALL STREET | 11 | 132 | Cornwall Street | CREYKE BECK | HU8 8AQ | CT (DFES) | 32.4117 | 32.3607 | 32.2967 | 32.2247 | 32.1177 | 31.9627 | 31.8037 | 31.6427 | 31.4657 | 31.2787 | 30.2607 | 29.1697 | 28.0657 | 26.9887 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CORRINGHAM ROAD | 11 | 33 | Blyton | KEADBY | DN21 1FT | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COSTHORPE | 11 | 66 | Thurcroft | THURCROFT | S81 9QR | CT (DFES) | 6.6471 | 6.6051 | 6.5501 | 6.4861 | 6.4031 | 6.2861 | 6.1631 | 6.0331 | 5.8841 | 5.7181 | 4.7791 | 3.8971 | 2.9701 | 2.0541 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COUNTY ROAD NORTH | 11 | 33 | Hull South | CREYKE BECK | HU5 5DR | CT (DFES) | 8.1964 | 8.0064 | 7.7634 | 7.4914 | 7.0984 | 6.5294 | 5.9454 | 5.3434 | 4.6714 | 3.9514 | 0.0074049 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CRACOE | 11 | 33 | Silsden | BRADFORD WEST | BD23 6BE | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROOKESMOOR ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 3FP | CT (DFES) | 3.5057 | 3.3717 | 3.2017 | 3.0117 | 2.7327 | 2.3247 | 1.9097 | 1.4847 | 1.0147 | 0.51671 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROSSHILLS | 11 | 33 | Silsden | BRADFORD WEST | BD20 7AQ | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROWLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN17 4BB | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROWN STREET | 11 | 33 | Girlington | BRADFORD WEST | BD1 2LA | CT (DFES) | 0.77471 | 0.76071 | 0.74171 | 0.72171 | 0.69071 | 0.64671 | 0.60171 | 0.55571 | 0.50471 | 0.45071 | 0.15571 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DALTON | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD2 1FF | CT (DFES) | 2.631 | 2.485 | 2.3 | 2.092 | 1.788 | 1.346 | 0.894 | 0.432 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DARNALL | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 4JT | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DEARNE ROAD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DG | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DEIGHTON | 11 | 33 | Brighouse 132/33kV | ELLAND | HD2 1UP | CT (DFES) | 18.408 | 18.324 | 18.218 | 18.099 | 17.926 | 17.673 | 17.414 | 17.149 | 16.856 | 16.543 | 14.841 | 13.028 | 11.189 | 9.39 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENBY DALE ROAD | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7BH | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENBY GRANGE | 11 | 33 | Thornhill 132kV | ELLAND | WF4 4JG | CT (DFES) | 0.30811 | 0.27911 | 0.24311 | 0.20211 | 0.14311 | 0.05711 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENHOLME | 11 | 33 | Holmfield | BRADFORD WEST | BD13 4JF | CT (DFES) | 11.5867 | 11.5567 | 11.5187 | 11.4757 | 11.4137 | 11.3217 | 11.2287 | 11.1327 | 11.0267 | 10.9147 | 10.3047 | 9.6517 | 8.9907 | 8.3447 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DINNINGTON | 11 | 66 | Thurcroft | THURCROFT | S25 3QT | CT (DFES) | 0 | 22.3047 | 22.1577 | 21.9917 | 21.7537 | 21.4087 | 21.0557 | 20.6927 | 20.2897 | 19.8577 | 17.4887 | 15.0247 | 12.5107 | 10.0517 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DOUGHTY ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN32 0LR | CT (DFES) | 3.8098 | 3.6468 | 3.4368 | 3.2008 | 2.8598 | 2.3678 | 1.8638 | 1.3468 | 0.7718 | 0.1568 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DOWKER STREET | 11 | 33 | Lindley | ELLAND | HD3 4JB | CT (DFES) | 0.47851 | 0.40151 | 0.30451 | 0.19551 | 0.035515 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRAX PRIMARY | 11 | 66 | Camblesforth | CAMBLESFORTH | YO8 6PQ | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 5XR | CT (DFES) | 13.7825 | 13.5535 | 13.2595 | 12.9295 | 12.4795 | 11.8335 | 11.1555 | 10.4365 | 9.6165 | 8.7145 | 3.6785 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRONFIELD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S18 2XU | CT (DFES) | 1.6672 | 1.6082 | 1.5342 | 1.4502 | 1.3302 | 1.1552 | 0.9762 | 0.7902 | 0.5832 | 0.3612 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DUDLEY HILL | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9NW | CT (DFES) | 23.1348 | 23.0748 | 22.9988 | 22.9138 | 22.7898 | 22.6078 | 22.4218 | 22.2328 | 22.0228 | 21.7998 | 20.5878 | 19.2908 | 17.9778 | 16.6948 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DUNKESWICK | 11 | 33 | Bramham | FERRYBRIDGE B | LS17 9LP | CT (DFES) | 12.0343 | 11.9743 | 11.8923 | 11.7983 | 11.6793 | 11.5233 | 11.3563 | 11.1763 | 10.9683 | 10.7293 | 9.3443 | 8.1853 | 6.9273 | 5.6823 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DURKAR LOW LANE | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF4 3BJ | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EASINGTON | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0SU | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EASTFIELD ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LW | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ECCLESFIELD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 9YR | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EDLINGTON | 11 | 66 | Thurcroft | THURCROFT | DN12 1SU | CT (DFES) | 13.5315 | 13.3945 | 13.2195 | 13.0225 | 12.7405 | 12.3325 | 11.9135 | 11.4805 | 10.9965 | 10.4775 | 7.6245 | 4.6545 | 1.6225 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EGGBOROUGH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | DN14 0QA | CT (DFES) | 7.4226 | 7.3976 | 7.3646 | 7.3276 | 7.2766 | 7.2056 | 7.1296 | 7.0496 | 6.9586 | 6.8566 | 6.2916 | 5.7256 | 5.1396 | 4.5616 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELGAR ROAD | 11 | 33 | Hull West | CREYKE BECK | HU4 7NY | CT (DFES) | 21.9047 | 21.7127 | 21.4677 | 21.1917 | 20.8077 | 20.2537 | 19.6767 | 19.0727 | 18.3907 | 17.6467 | 13.5277 | 9.2987 | 4.9577 | 0.68271 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLAND 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX5 9AE | CT (DFES) | 19.9595 | 19.8875 | 19.7945 | 19.6915 | 19.5415 | 19.3225 | 19.0975 | 18.8665 | 18.6085 | 18.3335 | 16.8325 | 15.2245 | 13.5945 | 11.9965 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIFOOT LANE | 11 | 33 | Saltend 132/33kV | SALTEND NORTH | HU12 9EB | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 1/3 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | CT (DFES) | 4.7828 | 4.7298 | 4.6618 | 4.5868 | 4.4748 | 4.3128 | 4.1468 | 3.9778 | 3.7898 | 3.5908 | 2.5098 | 1.3528 | 0.18077 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 2 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 1 | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 4LS | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 2 | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S75 4LS | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELSECAR | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S74 8AU | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ENDIKE LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 8AY | CT (DFES) | 16.4794 | 16.3624 | 16.2114 | 16.0424 | 15.8004 | 15.4504 | 15.0894 | 14.7164 | 14.2994 | 13.8514 | 11.3904 | 8.8164 | 6.1904 | 3.6154 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EPWORTH | 11 | 33 | Blyton | KEADBY | DN9 1JU | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FARNLEY CRESCENT | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 5AN | CT (DFES) | 0.80408 | 0.70108 | 0.56908 | 0.42208 | 0.20708 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FENTON LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6EZ | CT (DFES) | 5.0852 | 5.0462 | 4.9962 | 4.9402 | 4.8632 | 4.7552 | 4.6402 | 4.5192 | 4.3802 | 4.2262 | 3.3692 | 2.5112 | 1.6232 | 0.74518 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF11 8RR | CT (DFES) | 2.099 | 1.906 | 1.657 | 1.377 | 0.981 | 0.41 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIR TREE LANE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS17 7BZ | CT (DFES) | 3.8168 | 3.6878 | 3.5218 | 3.3368 | 3.0648 | 2.6708 | 2.2678 | 1.8548 | 1.3988 | 0.91376 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIRST AVENUE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 9NE | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIRTH BROWN | 11 | 33 | Santon | KEADBY | DN16 1XP | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FISH DAM LANE | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 3HQ | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FLIXBOROUGH | 11 | 33 | Scunthorpe North | KEADBY | DN15 8RR | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOLLY HALL | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 3TF | CT (DFES) | 1.7827 | 1.7207 | 1.6417 | 1.5527 | 1.4237 | 1.2347 | 1.0417 | 0.8447 | 0.6257 | 0.3927 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOUR LANE ENDS | 11 | 33 | Girlington | BRADFORD WEST | BD8 0LJ | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOXHILLS | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FULLERTON ROAD | 11 | 33 | Templeborough 275/33KV | TEMPLEBOROUGH 275/33KV | S60 1DL | CT (DFES) | 0.09287 | 0.04687 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FURNESS AVENUE | 11 | 33 | Holmfield | BRADFORD WEST | WF8 3JA | CT (DFES) | 1.0899 | 0.97686 | 0.83286 | 0.67286 | 0.43986 | 0.098864 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GAISBY LANE | 11 | 33 | Bradford | BRADFORD WEST | BD2 1BB | CT (DFES) | 3.086 | 2.979 | 2.843 | 2.69 | 2.466 | 2.139 | 1.805 | 1.464 | 1.087 | 0.68598 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIBRALTAR ROAD | 11 | 33 | Holmfield | BRADFORD WEST | HX1 4HL | CT (DFES) | 4.2651 | 4.1091 | 3.9111 | 3.6891 | 3.3681 | 2.8981 | 2.4151 | 1.9181 | 1.3641 | 0.7731 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIBSON LANE | 11 | 33 | Hull West | CREYKE BECK | HU14 3HH | CT (DFES) | 17.016 | 16.843 | 16.622 | 16.374 | 16.034 | 15.548 | 15.037 | 14.496 | 13.878 | 13.198 | 9.405 | 5.569 | 1.61 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GILDERSOME | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 7HW | CT (DFES) | 0.63387 | 0.57587 | 0.50087 | 0.41687 | 0.29387 | 0.11587 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GLEADLESS VALLEY | 11 | 33 | Norton Lees | NORTON LEES | S14 1FP | CT (DFES) | 1.728 | 1.618 | 1.477 | 1.319 | 1.088 | 0.74998 | 0.40498 | 0.052984 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GOOLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 6SX | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GRAINTHORPE | 11 | 33 | Wold Newton | KEADBY | LN11 7JU | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREAT COATES | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN37 9PN | CT (DFES) | 2.1241 | 1.9981 | 1.8351 | 1.6511 | 1.3881 | 1.0091 | 0.62009 | 0.21909 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREENHILL | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 7RJ | CT (DFES) | 0.84323 | 0.77723 | 0.69323 | 0.60023 | 0.46223 | 0.26223 | 0.058233 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS RD | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GRIMETHORPE | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S72 7BQ | CT (DFES) | 15.5259 | 15.4659 | 15.3899 | 15.3039 | 15.1809 | 15.0029 | 14.8199 | 14.6309 | 14.4209 | 14.1959 | 12.9599 | 11.6739 | 10.3619 | 9.0759 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GROVE STREET | 11 | 33 | Lindley | ELLAND | HD1 2PB | CT (DFES) | 13.6692 | 13.6482 | 13.6212 | 13.5912 | 13.5472 | 13.4832 | 13.4182 | 13.3512 | 13.2762 | 13.1972 | 12.7662 | 12.3072 | 11.8412 | 11.3862 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GUARDIAN GLASS | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8GA | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HACKENTHORPE | 11 | 66 | Thurcroft | THURCROFT | S12 4ET | CT (DFES) | 24.1746 | 24.0626 | 23.9196 | 23.7606 | 23.5256 | 23.1826 | 22.8336 | 22.4766 | 22.0816 | 21.6626 | 19.3846 | 16.9446 | 14.4736 | 12.0606 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 33/11KV | 11 | 33 | Halifax 132/33kV | ELLAND | HX1 1XB | CT (DFES) | 2.3676 | 2.2646 | 2.1346 | 1.9896 | 1.7776 | 1.4686 | 1.1516 | 0.82462 | 0.46062 | 0.072619 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALLAM STREET | 11 | 33 | Menston | BRADFORD WEST | LS20 8AG | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARDEN | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 1BG | CT (DFES) | 6.1233 | 6.0913 | 6.0503 | 6.0053 | 5.9383 | 5.8403 | 5.7403 | 5.6383 | 5.5253 | 5.4053 | 4.7533 | 4.0553 | 3.3483 | 2.6583 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARPSWELL | 11 | 33 | Blyton | KEADBY | DN21 5UT | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARWORTH | 11 | 66 | Thurcroft | THURCROFT | DN11 8JW | CT (DFES) | 19.5555 | 19.5015 | 19.4315 | 19.3525 | 19.2435 | 19.0895 | 18.9285 | 18.7605 | 18.5695 | 18.3615 | 17.1975 | 16.0505 | 14.8625 | 13.6925 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 1 | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD22 9EP | CT (DFES) | 13.6516 | 13.6026 | 13.5396 | 13.4706 | 13.3676 | 13.2186 | 13.0656 | 12.9096 | 12.7376 | 12.5536 | 11.5576 | 10.4916 | 9.4116 | 8.3576 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 2 | 11 | 33 | Silsden | BRADFORD WEST | BD22 9EP | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAXEY | 11 | 33 | Blyton | KEADBY | DN9 2LT | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAYTON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1RJ | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 15.9815 | 15.7345 | 15.3805 | 15.0095 | 14.6155 | 14.1665 | 13.6725 | 10.9155 | 8.1275 | 5.2495 | 2.4075 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAZLEHEAD | 11 | 33 | Thornhill 132kV | ELLAND | S36 4HG | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEBDEN BRIDGE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 6LX | CT (DFES) | 7.4787 | 7.4477 | 7.4077 | 7.3627 | 7.2987 | 7.2037 | 7.1067 | 7.0067 | 6.8957 | 6.7767 | 6.1277 | 5.4327 | 4.7277 | 4.0367 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEDLEY CHASE | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 1YN | CT (DFES) | 12.6838 | 12.6598 | 12.6278 | 12.5928 | 12.5408 | 12.4648 | 12.3878 | 12.3098 | 12.2228 | 12.1298 | 11.6248 | 11.0878 | 10.5438 | 10.0118 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEDON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 8ED | CT (DFES) | 11.4075 | 11.3995 | 11.3895 | 11.3785 | 11.3625 | 11.3385 | 11.3145 | 11.2895 | 11.2625 | 11.2335 | 11.0775 | 10.9095 | 10.7405 | 10.5745 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEMSWORTH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 5BZ | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 1 | 11 | 33 | Hull South | CREYKE BECK | HU4 6SP | CT (DFES) | 0.84984 | 0.80384 | 0.74484 | 0.67884 | 0.58684 | 0.45484 | 0.31684 | 0.17184 | 0.0088392 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 2 | 11 | 33 | Hull West | CREYKE BECK | HU4 6SP | CT (DFES) | 1.4755 | 1.4315 | 1.3755 | 1.3125 | 1.2235 | 1.0955 | 0.96352 | 0.82552 | 0.66952 | 0.50052 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HIBALDSTOW | 11 | 33 | Santon | KEADBY | DN21 4NH | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HICKLETON | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 0DE | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HILLCREST | 11 | 33 | Leeds East | SKELTON GRANGE | LS8 3AA | CT (DFES) | 3.4569 | 3.3329 | 3.1749 | 2.9969 | 2.7379 | 2.3599 | 1.9739 | 1.5799 | 1.1429 | 0.67893 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLBECK | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9SZ | CT (DFES) | 4.014 | 3.92 | 3.798 | 3.663 | 3.464 | 3.175 | 2.88 | 2.578 | 2.244 | 1.889 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLDERNESS | 11 | 33 | Bransholme | CREYKE BECK | HU9 4AU | CT (DFES) | 0.065508 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 4BX | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 20.3205 | 20.1705 | 20.0105 | 19.8285 | 19.6285 | 18.5075 | 17.3785 | 16.2125 | 15.0605 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HONLEY | 11 | 33 | Lindley | ELLAND | HD9 6RU | CT (DFES) | 10.3769 | 10.2749 | 10.1459 | 10.0009 | 9.7889 | 9.4799 | 9.1649 | 8.8419 | 8.4829 | 8.1029 | 6.0269 | 3.8149 | 1.5709 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOPE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S33 6RP | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HORBURY | 11 | 33 | Thornhill 132kV | ELLAND | WF4 6EU | CT (DFES) | 17.9233 | 17.8203 | 17.6853 | 17.5353 | 17.3183 | 17.0053 | 16.6853 | 16.3563 | 15.9903 | 15.5983 | 13.4473 | 11.2193 | 8.9433 | 6.7163 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOUGHTON MAIN | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S72 0GX | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 33/11KV | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5NP | CT (DFES) | 22.6786 | 22.5386 | 22.3586 | 22.1566 | 21.8776 | 21.4776 | 21.0586 | 20.6176 | 20.1156 | 19.5666 | 16.5116 | 13.4016 | 10.1986 | 7.0396 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUMBER ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LZ | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNMANBY | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO14 0JY | CT (DFES) | 20.2125 | 20.1215 | 19.9975 | 19.8545 | 19.6765 | 19.4385 | 19.1825 | 18.9035 | 18.5795 | 18.2055 | 16.0485 | 14.1785 | 12.1655 | 10.1665 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ICI FIBRES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4LT | CT (DFES) | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IDLE | 11 | 33 | Bradford | BRADFORD WEST | BD10 8SA | CT (DFES) | 2.5981 | 2.4821 | 2.3341 | 2.1691 | 1.9261 | 1.5711 | 1.2101 | 0.84005 | 0.43105 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ILKLEY | 11 | 33 | Silsden | BRADFORD WEST | LS29 9BE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | INGS LANE | 11 | 33 | Silsden | BRADFORD WEST | BD23 1UP | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | 0.012462 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IVESON HOUSE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 6RF | CT (DFES) | 20.8306 | 20.7136 | 20.5646 | 20.3976 | 20.1526 | 19.7966 | 19.4326 | 19.0616 | 18.6496 | 18.2116 | 15.8276 | 13.2926 | 10.7216 | 8.2086 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | JARRATT STREET | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN1 2BS | CT (DFES) | 13.0728 | 12.9998 | 12.9058 | 12.7998 | 12.6488 | 12.4308 | 12.2058 | 11.9738 | 11.7148 | 11.4368 | 9.9088 | 8.3178 | 6.6938 | 5.1018 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KEDDINGTON ROAD | 11 | 33 | Wold Newton | KEADBY | LN11 0DE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KEIGHLEY | 11 | 132 | Keighley | BRADFORD WEST | BD21 5AJ | CT (DFES) | 30.3919 | 30.3269 | 30.2439 | 30.1509 | 30.0139 | 29.8149 | 29.6119 | 29.4049 | 29.1749 | 28.9309 | 27.6039 | 26.1859 | 24.7479 | 23.3439 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KENMORE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 0XE | CT (DFES) | 18.8639 | 18.8169 | 18.7559 | 18.6869 | 18.5889 | 18.4459 | 18.3009 | 18.1509 | 17.9849 | 17.8069 | 16.8289 | 15.8159 | 14.7819 | 13.7699 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KILLINGHALL ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD3 8HN | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KILNHURST | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S64 5TL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KING GEORGE DOCK | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5PL | CT (DFES) | 23.856 | 23.85 | 23.843 | 23.834 | 23.822 | 23.804 | 23.785 | 23.766 | 23.746 | 23.724 | 23.605 | 23.477 | 23.348 | 23.222 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRK DRIVE | 11 | 33 | Menston | BRADFORD WEST | BD17 6SA | CT (DFES) | 1.0234 | 0.94338 | 0.84238 | 0.72838 | 0.56138 | 0.31838 | 0.070381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRK SANDALL | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 1QP | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKBURN | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 9EH | CT (DFES) | 6.1362 | 6.0872 | 6.0242 | 5.9532 | 5.8572 | 5.7222 | 5.5802 | 5.4282 | 5.2542 | 5.0612 | 3.9762 | 2.9132 | 1.8062 | 0.71225 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIVETON PARK | 11 | 66 | Thurcroft | THURCROFT | S26 6RP | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KNOSTROP | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0PJ | CT (DFES) | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEA ROAD | 11 | 33 | Blyton | KEADBY | DN21 1ND | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEASOWE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 2EY | CT (DFES) | 6.817 | 6.755 | 6.675 | 6.585 | 6.455 | 6.264 | 6.07 | 5.871 | 5.651 | 5.418 | 4.143 | 2.789 | 1.415 | 0.072016 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEDSTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF10 2AX | CT (DFES) | 1.2728 | 1.1808 | 1.0628 | 0.9308 | 0.7388 | 0.4588 | 0.1728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS ROAD | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 5AA | CT (DFES) | 0.37149 | 0.33149 | 0.28149 | 0.22449 | 0.14049 | 0.019491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEGRAMS MILL LANE | 11 | 33 | Girlington | BRADFORD WEST | BD7 2BA | CT (DFES) | 21.2118 | 21.1448 | 21.0598 | 20.9648 | 20.8248 | 20.6208 | 20.4128 | 20.1998 | 19.9648 | 19.7148 | 18.3568 | 16.9038 | 15.4318 | 13.9928 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEYLANDS ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS2 7QB | CT (DFES) | 16.1422 | 16.1242 | 16.1002 | 16.0742 | 16.0362 | 15.9802 | 15.9232 | 15.8652 | 15.8012 | 15.7322 | 15.3592 | 14.9622 | 14.5602 | 14.1662 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LIVERSEDGE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF15 7NY | CT (DFES) | 1.7459 | 1.6749 | 1.5849 | 1.4839 | 1.3349 | 1.1199 | 0.89888 | 0.67288 | 0.42288 | 0.15588 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOUTH | 11 | 33 | Wold Newton | KEADBY | LN11 0WA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOW MOOR | 11 | 33 | Staygate | SKELTON GRANGE | BD12 0NG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOWFIELDS | 11 | 33 | Brighouse 132/33kV | ELLAND | HX5 9DE | CT (DFES) | 25.256 | 25.254 | 25.251 | 25.247 | 25.242 | 25.235 | 25.227 | 25.219 | 25.21 | 25.201 | 25.15 | 25.095 | 25.04 | 24.985 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOXLEY ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 6SJ | CT (DFES) | 0.24526 | 0.23926 | 0.23126 | 0.22126 | 0.20826 | 0.18826 | 0.16826 | 0.14826 | 0.12526 | 0.10126 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANCHESTER ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD5 0QL | CT (DFES) | 3.0757 | 3.0557 | 3.0307 | 3.0017 | 2.9597 | 2.8977 | 2.8347 | 2.7707 | 2.6997 | 2.6247 | 2.2147 | 1.7757 | 1.3317 | 0.89768 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 1 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S12 2DL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 2 | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S12 2DL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARKHAM GATES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 2FS | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARMION ROAD | 11 | 33 | Norton Lees | NORTON LEES | S11 8TS | CT (DFES) | 2.5738 | 2.4288 | 2.2438 | 2.0378 | 1.7338 | 1.2908 | 0.8388 | 0.3778 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARSDEN ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN31 3SQ | CT (DFES) | 4.9919 | 4.9279 | 4.8459 | 4.7539 | 4.6209 | 4.4289 | 4.2319 | 4.0299 | 3.8049 | 3.5649 | 2.2479 | 0.8739 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARTONGATE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 6RX | CT (DFES) | 0 | 0 | 0 | 18.7505 | 18.3185 | 17.6985 | 17.0485 | 16.3595 | 15.5735 | 14.7075 | 9.8775 | 4.9945 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MELTHAM | 11 | 33 | Lindley | ELLAND | HD9 4AL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MEXBOROUGH 1_2 | 11 | 66 | Thurcroft | THURCROFT | S64 0JD | CT (DFES) | 24.566 | 24.375 | 24.13 | 23.854 | 23.459 | 22.889 | 22.302 | 21.696 | 21.02 | 20.294 | 16.305 | 12.152 | 7.912 | 3.757 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MIDDLETON TOWN STREET | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS10 3TQ | CT (DFES) | 16.348 | 16.245 | 16.113 | 15.966 | 15.75 | 15.436 | 15.116 | 14.788 | 14.425 | 14.039 | 11.936 | 9.702 | 7.435 | 5.219 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILLHOUSES | 11 | 33 | Jordanthorpe | JORDANTHORPE | S7 2QH | CT (DFES) | 1.2525 | 1.1995 | 1.1325 | 1.0575 | 0.94652 | 0.78452 | 0.62052 | 0.45152 | 0.26552 | 0.067523 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILLROYD STREET | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1JZ | CT (DFES) | 14.2727 | 14.1687 | 14.0377 | 13.8917 | 13.6787 | 13.3677 | 13.0487 | 12.7197 | 12.3537 | 11.9627 | 9.8307 | 7.5457 | 5.2297 | 2.9597 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILTON PLACE | 11 | 33 | Wakefield North | SKELTON GRANGE | WF5 9EG | CT (DFES) | 18.6287 | 18.5007 | 18.3357 | 18.1497 | 17.8817 | 17.4957 | 17.0997 | 16.6927 | 16.2417 | 15.7577 | 13.1077 | 10.3507 | 7.5377 | 4.7867 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MIRFIELD | 11 | 33 | Thornhill 132kV | ELLAND | WF14 8NF | CT (DFES) | 19.518 | 19.391 | 19.229 | 19.047 | 18.781 | 18.394 | 17.999 | 17.594 | 17.144 | 16.667 | 14.063 | 11.29 | 8.477 | 5.726 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MONCKTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S71 4BG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOOR ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS6 4BJ | CT (DFES) | 23.1946 | 23.0606 | 22.8886 | 22.6966 | 22.4166 | 22.0076 | 21.5906 | 21.1646 | 20.6916 | 20.1896 | 17.4546 | 14.5476 | 11.5976 | 8.7146 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOORSIDE ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD2 3RJ | CT (DFES) | 20.1619 | 20.0399 | 19.8849 | 19.7109 | 19.4559 | 19.0839 | 18.7049 | 18.3169 | 17.8879 | 17.4329 | 14.9549 | 12.3049 | 9.6199 | 6.9969 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MORLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 9HS | CT (DFES) | 19.8137 | 19.7117 | 19.5827 | 19.4377 | 19.2257 | 18.9177 | 18.6027 | 18.2807 | 17.9237 | 17.5447 | 15.4787 | 13.2837 | 11.0567 | 8.8797 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOUNT STREET | 11 | 33 | Bradford | BRADFORD WEST | BD4 8TB | CT (DFES) | 21.003 | 20.974 | 20.937 | 20.895 | 20.835 | 20.746 | 20.656 | 20.564 | 20.461 | 20.353 | 19.763 | 19.132 | 18.492 | 17.867 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MYTHOLMROYD | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 8NE | CT (DFES) | 13.7561 | 13.6991 | 13.6261 | 13.5451 | 13.4281 | 13.2551 | 13.0791 | 12.8961 | 12.6931 | 12.4771 | 11.2951 | 10.0281 | 8.7431 | 7.4841 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NAB LANE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 9NE | CT (DFES) | 11.9786 | 11.9146 | 11.8336 | 11.7426 | 11.6096 | 11.4156 | 11.2176 | 11.0146 | 10.7906 | 10.5506 | 9.2476 | 7.8586 | 6.4506 | 5.0736 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NABWOOD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD18 4AA | CT (DFES) | 13.3961 | 13.3021 | 13.1831 | 13.0481 | 12.8521 | 12.5651 | 12.2721 | 11.9731 | 11.6421 | 11.2901 | 9.3781 | 7.3331 | 5.2611 | 3.2371 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NATIONAL AVENUE | 11 | 33 | Hull South | CREYKE BECK | HU5 4JN | CT (DFES) | 0.76537 | 0.71037 | 0.63837 | 0.55937 | 0.44137 | 0.26937 | 0.094373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | Wincobank | WINCOBANK | S61 2DL | CT (DFES) | 18.9252 | 18.8352 | 18.7202 | 18.5912 | 18.4052 | 18.1372 | 17.8622 | 17.5792 | 17.2642 | 16.9272 | 15.0802 | 13.1602 | 11.2002 | 9.2822 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEW ORCHARD LANE | 11 | 66 | Thurcroft | THURCROFT | S66 9HY | CT (DFES) | 1.1972 | 1.1202 | 1.0202 | 0.90815 | 0.74715 | 0.51515 | 0.27615 | 0.031153 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWHALL ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 2RS | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1743 | 1.0753 | 0.9703 | 0.3993 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 1 | 11 | 33 | Hull West | CREYKE BECK | HU15 2QU | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 2 | 11 | 33 | Osgodby 3/4 | DRAX | HU15 2QU | CT (DFES) | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NINELANDS LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS25 2PE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORFOLK PARK | 11 | 33 | Norton Lees | NORTON LEES | S2 3UU | CT (DFES) | 0.57439 | 0.46639 | 0.32839 | 0.17439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORMANBY | 11 | 33 | Blyton | KEADBY | LN8 2HQ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORMANTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF6 2JA | CT (DFES) | 4.5837 | 4.4847 | 4.3587 | 4.2167 | 4.0117 | 3.7167 | 3.4147 | 3.1037 | 2.7587 | 2.3887 | 0.3587 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORTH AVENUE | 11 | 33 | Menston | BRADFORD WEST | LS21 1SX | CT (DFES) | 19.1876 | 19.0966 | 18.9806 | 18.8506 | 18.6616 | 18.3846 | 18.1026 | 17.8136 | 17.4946 | 17.1546 | 15.3036 | 13.3356 | 11.3396 | 9.3886 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORTH THORESBY | 11 | 33 | Wold Newton | KEADBY | DN36 5SB | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORWOOD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 9JR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OAKES ROAD | 11 | 33 | Lindley | ELLAND | HD3 3EW | CT (DFES) | 2.4988 | 2.3878 | 2.2458 | 2.0878 | 1.8558 | 1.5178 | 1.1718 | 0.81882 | 0.42582 | 0.0088215 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OAKWOOD LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 3LF | CT (DFES) | 19.5501 | 19.4691 | 19.3651 | 19.2491 | 19.0791 | 18.8321 | 18.5801 | 18.3221 | 18.0361 | 17.7321 | 16.0781 | 14.3191 | 12.5351 | 10.7911 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ODSAL | 11 | 33 | Staygate | SKELTON GRANGE | BD6 1BW | CT (DFES) | 2.6556 | 2.5536 | 2.4226 | 2.2766 | 2.0626 | 1.7496 | 1.4306 | 1.1046 | 0.7436 | 0.3606 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OLYMPIA MILLS | 11 | 33 | Osgodby 3/4 | DRAX | YO8 7AG | CT (DFES) | 19.7551 | 19.6101 | 19.4231 | 19.2131 | 18.9271 | 18.5201 | 18.0921 | 17.6371 | 17.1181 | 16.5441 | 13.3371 | 10.1251 | 6.8011 | 3.5161 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ORGREAVE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 9NA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OUTWOOD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF3 3TA | CT (DFES) | 1.7967 | 1.6927 | 1.5597 | 1.4107 | 1.1947 | 0.88266 | 0.56266 | 0.23466 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK HILL | 11 | 33 | Sheffield City | SHEFFIELD CITY | S2 5QY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0562 | 0.90223 | 0.74023 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK ROAD | 11 | 33 | Thornhill 132kV | ELLAND | WF12 9LW | CT (DFES) | 1.1548 | 1.0638 | 0.94783 | 0.81683 | 0.62683 | 0.34883 | 0.065826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK STREET | 11 | 132 | Park Street | WEST MELTON / THORPE MARSH | S61 1TF | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PASTURE ROAD SOUTH | 11 | 33 | Santon | KEADBY | DN18 5RX | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PATRINGTON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0AD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 6BG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 2FL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PLANGEO | 11 | 33 | Hull South | CREYKE BECK | HU3 6EG | CT (DFES) | 3.5474 | 3.4324 | 3.2874 | 3.1244 | 2.8834 | 2.5324 | 2.1754 | 1.8114 | 1.4114 | 0.98737 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | POLLINGTON | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | DN14 0RR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0JG | CT (DFES) | 1.7338 | 1.7068 | 1.6728 | 1.6348 | 1.5778 | 1.4968 | 1.4128 | 1.3278 | 1.2328 | 1.1318 | 0.58376 | 0.0017583 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | POOL | 11 | 33 | Menston | BRADFORD WEST | LS21 1RP | CT (DFES) | 16.3885 | 16.3685 | 16.3425 | 16.3135 | 16.2735 | 16.2145 | 16.1545 | 16.0925 | 16.0225 | 15.9475 | 15.5335 | 15.1135 | 14.6835 | 14.2605 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PRINCE OF WALES | 11 | 33 | Featherstone | FERRYBRIDGE B | WF8 4PR | CT (DFES) | 10.8515 | 10.7395 | 10.5945 | 10.4315 | 10.1975 | 9.8605 | 9.5145 | 9.1595 | 8.7645 | 8.3415 | 6.0185 | 3.6135 | 1.1565 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PROSPECT ROAD | 11 | 33 | Lindley | ELLAND | HD3 4UY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | QUEENS ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 2LZ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | QUEENSBURY | 11 | 33 | Holmfield | BRADFORD WEST | HX3 7TJ | CT (DFES) | 25.4894 | 25.3514 | 25.1754 | 24.9784 | 24.6914 | 24.2714 | 23.8424 | 23.4014 | 22.9124 | 22.3914 | 19.5534 | 16.5144 | 13.4344 | 10.4204 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWCLIFFE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8PQ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWDON | 11 | 33 | Rodley | SKELTON GRANGE | LS19 7BZ | CT (DFES) | 23.8506 | 23.7596 | 23.6426 | 23.5126 | 23.3216 | 23.0436 | 22.7606 | 22.4706 | 22.1486 | 21.8076 | 19.9476 | 17.9696 | 15.9636 | 14.0036 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | Rawmarsh Road 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | Rawmarsh Road 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON ROAD | 11 | 33 | Girlington | BRADFORD WEST | BD1 3SH | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON SPRING ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 1PD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9378 | 2.7678 | 2.5888 | 1.6118 | 0.56478 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | REVILL LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 7QX | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROCKWARE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4RH | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY LANE | 11 | 33 | Rodley | SKELTON GRANGE | LS13 1LJ | CT (DFES) | 0.73721 | 0.63421 | 0.50321 | 0.35621 | 0.14021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROMAN AVENUE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 2DY | CT (DFES) | 20.4816 | 20.3966 | 20.2866 | 20.1636 | 19.9846 | 19.7236 | 19.4566 | 19.1836 | 18.8816 | 18.5606 | 16.8116 | 14.9526 | 13.0666 | 11.2236 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROYDS LANE | 11 | 33 | Wakefield North | SKELTON GRANGE | LS26 0BE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | CT (DFES) | 11.9028 | 11.8698 | 11.8258 | 11.7778 | 11.7068 | 11.6038 | 11.4978 | 11.3898 | 11.2708 | 11.1428 | 10.4488 | 9.7098 | 8.9598 | 8.2268 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT STREET | 11 | 33 | Girlington | BRADFORD WEST | BD7 4EH | CT (DFES) | 12.4136 | 12.3536 | 12.2766 | 12.1906 | 12.0646 | 11.8806 | 11.6926 | 11.5006 | 11.2876 | 11.0626 | 9.8356 | 8.5226 | 7.1936 | 5.8946 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTERFORTH | 11 | 33 | Silsden | BRADFORD WEST | BB18 6JD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTERHEBBLE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX3 0QH | CT (DFES) | 19.5266 | 19.4216 | 19.2876 | 19.1386 | 18.9206 | 18.6036 | 18.2776 | 17.9416 | 17.5676 | 17.1686 | 14.9886 | 12.6526 | 10.2846 | 7.9636 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTSHOUSE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU8 9HR | CT (DFES) | 21.3382 | 21.2652 | 21.1702 | 21.0642 | 20.9082 | 20.6812 | 20.4492 | 20.2142 | 19.9542 | 19.6802 | 18.1902 | 16.5932 | 14.9782 | 13.4022 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SANDHILL LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO41 4DF | CT (DFES) | 0.3057 | 0.2727 | 0.2307 | 0.1837 | 0.1187 | 0.024702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAXON ROAD | 11 | 33 | Norton Lees | NORTON LEES | S8 0XQ | CT (DFES) | 2.2302 | 2.1272 | 1.9952 | 1.8472 | 1.6302 | 1.3132 | 0.99018 | 0.66018 | 0.29418 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCARTHO | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN33 3JL | CT (DFES) | 0.082354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCHOLES | 11 | 33 | Thornhill 132kV | ELLAND | HD9 1UG | CT (DFES) | 0.88313 | 0.80813 | 0.71213 | 0.60513 | 0.44913 | 0.22213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCISSETT | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCULCOATES A | 11 | 132 | Sculcoates A | CREYKE BECK | HU5 1DA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SEACROFT | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 1LU | CT (DFES) | 13.181 | 13.112 | 13.024 | 12.926 | 12.781 | 12.572 | 12.358 | 12.139 | 11.896 | 11.639 | 10.235 | 8.742 | 7.228 | 5.749 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SEATON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU11 5RQ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SELBY | 11 | 33 | Osgodby 3/4 | DRAX | YO8 8NB | CT (DFES) | 0.58457 | 0.34257 | 0.030572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SELBY ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS15 0QE | CT (DFES) | 19.9456 | 19.8316 | 19.6856 | 19.5216 | 19.2836 | 18.9356 | 18.5806 | 18.2176 | 17.8156 | 17.3886 | 15.0616 | 12.5876 | 10.0776 | 7.6246 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHARLSTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF4 1BE | CT (DFES) | 11.9907 | 11.8667 | 11.7077 | 11.5277 | 11.2687 | 10.8967 | 10.5147 | 10.1217 | 9.6857 | 9.2187 | 6.6537 | 3.9977 | 1.2847 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHEPCOTE TINSLEY | 11 | 33 | Wincobank | WINCOBANK | S9 1RF | CT (DFES) | 30.0977 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0957 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHERBURN | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6PL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHIPLEY | 11 | 33 | Bradford | BRADFORD WEST | DN21 5UT | CT (DFES) | 25.8965 | 25.8225 | 25.7275 | 25.6215 | 25.4665 | 25.2395 | 25.0085 | 24.7715 | 24.5095 | 24.2325 | 22.7205 | 21.1035 | 19.4655 | 17.8655 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHIRLAND LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3GD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILVER STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 2DU | CT (DFES) | 2.7553 | 2.7393 | 2.7183 | 2.6953 | 2.6613 | 2.6103 | 2.5593 | 2.5073 | 2.4493 | 2.3883 | 2.0553 | 1.6993 | 1.3373 | 0.98535 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILVERWOOD | 11 | 66 | Thurcroft | THURCROFT | S65 4PR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SKILLINGS LANE | 11 | 33 | Hull West | CREYKE BECK | HU15 1EQ | CT (DFES) | 2.3494 | 2.2654 | 2.1594 | 2.0394 | 1.8754 | 1.6404 | 1.3944 | 1.1334 | 0.83539 | 0.50739 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SKIPTON | 11 | 33 | Silsden | BRADFORD WEST | BD23 2RR | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SLAITHWAITE | 11 | 33 | Lindley | ELLAND | HD7 6LS | CT (DFES) | 0.76186 | 0.68686 | 0.58986 | 0.48186 | 0.32486 | 0.094862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SLEDMERE GARTH | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 5DS | CT (DFES) | 18.726 | 18.68 | 18.621 | 18.556 | 18.46 | 18.32 | 18.178 | 18.032 | 17.871 | 17.7 | 16.765 | 15.773 | 14.765 | 13.781 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SMITH STREET | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 2RY | CT (DFES) | 12.7049 | 12.6379 | 12.5509 | 12.4529 | 12.3129 | 12.1099 | 11.9009 | 11.6879 | 11.4499 | 11.1969 | 9.8069 | 8.3579 | 6.8809 | 5.4369 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SMITHY GREEN | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SNAITHING PARK ROAD | 11 | 33 | Norton Lees | NORTON LEES | S10 3LJ | CT (DFES) | 0.098323 | 0.0073228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SNELSINS LANE | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 3UH | CT (DFES) | 16.3306 | 16.2606 | 16.1716 | 16.0716 | 15.9266 | 15.7136 | 15.4966 | 15.2746 | 15.0286 | 14.7676 | 13.3416 | 11.8216 | 10.2796 | 8.7736 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH ELMSALL | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 2JH | CT (DFES) | 23.1264 | 23.0414 | 22.9324 | 22.8094 | 22.6324 | 22.3764 | 22.1154 | 21.8464 | 21.5474 | 21.2264 | 19.4684 | 17.6454 | 15.7844 | 13.9644 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH FERRIBY | 11 | 33 | Santon | KEADBY | DN18 6JL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH KIRKBY | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 3TJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH RESTON | 11 | 33 | Wold Newton | KEADBY | LN11 8JQ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH STREET | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 1AH | CT (DFES) | 7.6349 | 7.5499 | 7.4409 | 7.3199 | 7.1419 | 6.8809 | 6.6159 | 6.3449 | 6.0449 | 5.7259 | 3.9929 | 2.1389 | 0.26091 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHGATE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 3BE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 18.8746 | 18.6406 | 18.3916 | 18.1066 | 17.7946 | 16.0496 | 14.2856 | 12.4646 | 10.6666 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHWOOD ROAD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU16 5AN | CT (DFES) | 0.032507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EN | CT (DFES) | 24.1372 | 24.0172 | 23.8642 | 23.6942 | 23.4462 | 23.0832 | 22.7112 | 22.3272 | 21.9002 | 21.4442 | 18.9552 | 16.2882 | 13.5842 | 10.9342 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPARK MILL LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 0TT | CT (DFES) | 5.8132 | 5.6172 | 5.3652 | 5.0832 | 4.6972 | 4.1442 | 3.5632 | 2.9482 | 2.2472 | 1.4752 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPENBOROUGH | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 5BT | CT (DFES) | 16.5105 | 16.4065 | 16.2735 | 16.1245 | 15.9075 | 15.5905 | 15.2665 | 14.9355 | 14.5675 | 14.1765 | 12.0455 | 9.7755 | 7.4725 | 5.2205 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPRING MILL STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD5 7HF | CT (DFES) | 3.4728 | 3.4278 | 3.3698 | 3.3048 | 3.2088 | 3.0698 | 2.9278 | 2.7828 | 2.6218 | 2.4518 | 1.5248 | 0.53276 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAINFORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN7 5HG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAIRFOOT | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 5AD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STANLEY STREET | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S3 8HG | CT (DFES) | 3.1003 | 3.0683 | 3.0283 | 2.9833 | 2.9173 | 2.8213 | 2.7223 | 2.6223 | 2.5113 | 2.3933 | 1.7523 | 1.0653 | 0.3703 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STANNINGTON ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 5FH | CT (DFES) | 1.7126 | 1.5576 | 1.3606 | 1.1396 | 0.81562 | 0.34362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STATION ROAD | 11 | 33 | Scunthorpe North | KEADBY | DN15 6BT | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STEVENSON ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 3XG | CT (DFES) | 1.1752 | 1.1752 | 1.1742 | 1.1742 | 1.1742 | 1.1732 | 1.1732 | 1.1722 | 1.1722 | 1.1712 | 1.1672 | 1.1642 | 1.1602 | 1.1562 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOKE STREET | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3QN | CT (DFES) | 0.145 | 0.145 | 0.144 | 0.143 | 0.141 | 0.139 | 0.136 | 0.134 | 0.131 | 0.128 | 0.112 | 0.095 | 0.078 | 0.061 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 132/11KV | 11 | 132 | Stourton 132/11kV | SKELTON GRANGE | LS10 1SP | CT (DFES) | 1.2721 | 1.2701 | 1.2661 | 1.2621 | 1.2571 | 1.2491 | 1.2401 | 1.2321 | 1.2221 | 1.2121 | 1.1571 | 1.0991 | 1.0391 | 0.98212 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 33/11KV | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1AX | CT (DFES) | 5.587 | 5.544 | 5.49 | 5.429 | 5.34 | 5.21 | 5.078 | 4.943 | 4.793 | 4.634 | 3.766 | 2.844 | 1.909 | 0.99502 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOW | 11 | 33 | Blyton | KEADBY | LN1 2AJ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWAN BANK LANE | 11 | 33 | Halifax 132/33kV | ELLAND | HX3 9XT | CT (DFES) | 1.3633 | 1.2913 | 1.2013 | 1.0993 | 0.95235 | 0.73835 | 0.51835 | 0.29135 | 0.037346 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWEET STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9TZ | CT (DFES) | 7.644 | 7.632 | 7.617 | 7.6 | 7.575 | 7.539 | 7.502 | 7.464 | 7.422 | 7.378 | 7.135 | 6.877 | 6.615 | 6.359 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWINNOW MOOR | 11 | 33 | Rodley | SKELTON GRANGE | LS13 4RJ | CT (DFES) | 2.3145 | 2.2115 | 2.0785 | 1.9295 | 1.7125 | 1.3965 | 1.0735 | 0.74347 | 0.37747 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TADCASTER | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9PA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TANKERSLEY PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 2PT | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S60 1AD | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNBURY | 11 | 33 | Rodley | SKELTON GRANGE | BD3 7AD | CT (DFES) | 4.9733 | 4.8903 | 4.7843 | 4.6653 | 4.4913 | 4.2383 | 3.9793 | 3.7143 | 3.4213 | 3.1113 | 1.4193 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN8 4NA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNTON | 11 | 33 | Holmfield | BRADFORD WEST | BD13 3DP | CT (DFES) | 19.9012 | 19.7602 | 19.5812 | 19.3802 | 19.0862 | 18.6562 | 18.2182 | 17.7712 | 17.2752 | 16.7492 | 13.8872 | 10.8272 | 7.7262 | 4.6972 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORPE ROAD | 11 | 33 | Osgodby 3/4 | DRAX | DN14 7PA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TICKHILL ROAD | 11 | 66 | Thurcroft | THURCROFT | S66 7QN | CT (DFES) | 29.0194 | 28.8964 | 28.7374 | 28.5594 | 28.3044 | 27.9364 | 27.5584 | 27.1684 | 26.7344 | 26.2694 | 23.7104 | 21.0584 | 18.3484 | 15.6954 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINGLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | WF3 1SS | CT (DFES) | 0.055615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY PARK ROAD | 11 | 33 | Wincobank | WINCOBANK | S9 5DL | CT (DFES) | 2.8557 | 2.8497 | 2.8407 | 2.8317 | 2.8187 | 2.7997 | 2.7797 | 2.7597 | 2.7367 | 2.7127 | 2.5837 | 2.4457 | 2.3057 | 2.1687 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1TY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TIVERTON ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 4DA | CT (DFES) | 1.4151 | 1.3341 | 1.2291 | 1.1131 | 0.94114 | 0.69014 | 0.43514 | 0.17514 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TODMORDEN | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | OL14 7NB | CT (DFES) | 12.771 | 12.691 | 12.589 | 12.475 | 12.309 | 12.067 | 11.819 | 11.563 | 11.278 | 10.973 | 9.312 | 7.532 | 5.726 | 3.957 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TOLLER LANE | 11 | 33 | Girlington | BRADFORD WEST | BD9 5LE | CT (DFES) | 21.2422 | 21.1562 | 21.0462 | 20.9232 | 20.7422 | 20.4792 | 20.2112 | 19.9362 | 19.6322 | 19.3102 | 17.5562 | 15.6802 | 13.7802 | 11.9232 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TONG STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9PP | CT (DFES) | 3.2422 | 3.1962 | 3.1372 | 3.0722 | 2.9762 | 2.8362 | 2.6942 | 2.5482 | 2.3862 | 2.2152 | 1.2832 | 0.28618 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | UPPER BASINGHALL STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS1 5JS | CT (DFES) | 4.333 | 4.326 | 4.317 | 4.307 | 4.292 | 4.27 | 4.248 | 4.225 | 4.2 | 4.173 | 4.027 | 3.872 | 3.715 | 3.562 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | VARLEY STREET | 11 | 33 | Rodley | SKELTON GRANGE | LS28 6AN | CT (DFES) | 22.6544 | 22.5614 | 22.4434 | 22.3114 | 22.1184 | 21.8374 | 21.5514 | 21.2574 | 20.9334 | 20.5874 | 18.7064 | 16.7074 | 14.6784 | 12.6964 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | VICTORIA STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4DP | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33242 | 0.25742 | 0.17942 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WALESBY | 11 | 33 | Wold Newton | KEADBY | LN8 3UL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WARREN LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9NT | CT (DFES) | 3.8678 | 3.8438 | 3.8128 | 3.7778 | 3.7278 | 3.6548 | 3.5798 | 3.5028 | 3.4168 | 3.3258 | 2.8268 | 2.2998 | 1.7648 | 1.2408 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WATH UPON DEARNE | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DX | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | Wincobank | WINCOBANK | S60 5BL | CT (DFES) | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5026 | 30.5026 | 30.5026 | 30.5026 | 30.5006 | 30.4986 | 30.4976 | 30.4956 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAWNE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 5BT | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEELAND ROAD | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 0LA | CT (DFES) | 7.1541 | 7.1121 | 7.0581 | 31.1446 | 31.0566 | 30.9296 | 30.7996 | 30.6666 | 30.5176 | 30.3586 | 29.4856 | 28.5816 | 27.6576 | 26.7536 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WELLINGTON STREET | 11 | 33 | Featherstone | FERRYBRIDGE B | WF10 1NW | CT (DFES) | 12.9061 | 12.8351 | 12.7431 | 12.6401 | 12.4921 | 12.2791 | 12.0601 | 11.8361 | 11.5861 | 11.3181 | 9.8501 | 8.3301 | 6.7761 | 5.2571 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WESLEY CRESCENT | 11 | 33 | Humberston | GRIMSBY WEST | DN35 0JU | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST DOCKS | 11 | 33 | Hull South | CREYKE BECK | HU3 4UU | CT (DFES) | 1.7743 | 1.7703 | 1.7653 | 1.7603 | 1.7523 | 1.7413 | 1.7293 | 1.7173 | 1.7043 | 1.6903 | 1.6153 | 1.5343 | 1.4533 | 1.3733 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST END LANE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN11 0PU | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST MOOR PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3FE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST PARK | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 5PS | CT (DFES) | 7.0496 | 6.9766 | 6.8826 | 6.7776 | 6.6236 | 6.4006 | 6.1716 | 5.9386 | 5.6796 | 5.4046 | 3.9076 | 2.3156 | 0.70062 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WESTCOTT STREET | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU8 8JN | CT (DFES) | 0.91389 | 0.77989 | 0.60789 | 0.41589 | 0.13189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHEATACRE ROAD | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 2GQ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHEATLEY PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4PG | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHINGATE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 3QT | CT (DFES) | 19.8581 | 19.7971 | 19.7201 | 19.6331 | 19.5061 | 19.3211 | 19.1321 | 18.9391 | 18.7261 | 18.4991 | 17.2611 | 15.9461 | 14.6111 | 13.3081 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITE LEE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 8AF | CT (DFES) | 1.8795 | 1.7505 | 1.5865 | 1.4025 | 1.1345 | 0.7435 | 0.3445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | Low Road | SKELTON GRANGE | LS1 4HR | CT (DFES) | 7.774 | 7.771 | 7.767 | 7.762 | 7.755 | 7.746 | 7.736 | 7.725 | 7.714 | 7.702 | 7.636 | 7.566 | 7.495 | 7.426 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS1 4BN | CT (DFES) | 18.7009 | 18.6959 | 18.6889 | 18.6819 | 18.6709 | 18.6549 | 18.6389 | 18.6229 | 18.6039 | 18.5849 | 18.4789 | 18.3669 | 18.2529 | 18.1419 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WIBSEY | 11 | 33 | Staygate | SKELTON GRANGE | BD6 3BG | CT (DFES) | 0.55926 | 0.43626 | 0.28026 | 0.10526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WITHERNSEA | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU19 2QA | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOODCOCK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 5LL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOODSEATS | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 8QB | CT (DFES) | 2.1707 | 2.0717 | 1.9467 | 1.8057 | 1.5997 | 1.2987 | 0.99169 | 0.67869 | 0.33169 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOOLLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 5JE | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WORSBROUGH PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S70 5LY | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WRAWBY | 11 | 33 | Santon | KEADBY | DN20 8SX | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4BL | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YEW GREEN ROAD | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD4 5DD | CT (DFES) | 1.326 | 1.233 | 1.115 | 0.98297 | 0.78997 | 0.50797 | 0.21997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YORK ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 6TF | CT (DFES) | 20.7421 | 20.6311 | 20.4901 | 20.3321 | 20.1011 | 19.7641 | 19.4211 | 19.0701 | 18.6801 | 18.2671 | 16.0141 | 13.6191 | 11.1891 | 8.8141 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YORK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 3AZ | CT (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Consumer Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ANNFIELD | 66 | 132 | Annfield | STELLA SOUTH | DH9 7XW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BARRACK ROAD | 33 | 132 | Barrack Road | STELLA NORTH | NE4 6DB | ST (DFES) | 114.63 | 114.439 | 114.28 | 114.09 | 113.878 | 113.557 | 113.223 | 112.826 | 112.465 | 112.061 | 109.566 | 107.595 | 105.676 | 104.066 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER | 33 | 132 | Blucher | STELLA NORTH | NE15 9SD | ST (DFES) | 94.478 | 94.078 | 93.588 | 93.219 | 92.84 | 92.19 | 91.52 | 90.744 | 90.04 | 89.261 | 85.611 | 81.777 | 78.269 | 75.459 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD | 33 | 132 | Bowesfield | NORTON | TS18 3HP | ST (DFES) | 61.996 | 60.058 | 57.385 | 56.382 | 55.702 | 54.429 | 53.042 | 51.648 | 50.908 | 49.611 | 48.173 | 42.463 | 36.736 | 31.941 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CHIRTON GRANGE | 33 | 132 | Chirton Grange | TYNEMOUTH | NE29 8EY | ST (DFES) | 62.046 | 61.698 | 61.319 | 60.95 | 60.546 | 59.881 | 59.198 | 58.39 | 57.63 | 56.81 | 52.448 | 48.4 | 44.658 | 41.633 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | COALBURNS | 66 | 132 | Coalburns | STELLA SOUTH | NE40 4JP | ST (DFES) | 70.036 | 68.079 | 65.294 | 64.521 | 64.178 | 63.428 | 62.563 | 61.837 | 61.86 | 61.28 | 64.752 | 62.654 | 60.181 | 57.99 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL | 33 | 132 | Darlington Central | NORTON | DL1 1HG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON NORTH | 33 | 132 | Darlington North | NORTON | DL3 0XE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON | 66 | 132 | Dunston | STELLA NORTH | NE11 9DH | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH | 33 | 132 | Flatworth | TYNEMOUTH | NE29 7FN | ST (DFES) | 27.322 | 27.17 | 27.006 | 26.825 | 26.62 | 26.282 | 25.936 | 25.524 | 25.125 | 24.704 | 22.429 | 20.339 | 18.428 | 16.895 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH | 33 | 132 | Gosforth | TYNEMOUTH | NE3 1XL | ST (DFES) | 88.949 | 88.656 | 88.346 | 88.014 | 87.643 | 87.03 | 86.402 | 85.654 | 84.939 | 84.181 | 80.08 | 76.304 | 72.843 | 70.06 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/33KV | 33 | 132 | Harrogate 132/33kV | KNARESBOROUGH | HG1 2LA | ST (DFES) | 45.945 | 45.461 | 44.86 | 44.483 | 44.123 | 43.514 | 42.877 | 42.156 | 41.552 | 40.834 | 37.718 | 34.273 | 31.025 | 28.376 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE | 33 | 132 | Husthwaite | KNARESBOROUGH | YO61 4PN | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | Leeming Bar_Skeeby | NORTON | DL7 0RL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LINTON | 66 | 132 | Linton | BLYTH 132kV | NE61 5DA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALTON GRID | 66 | 132 | Malton Grid | OSBALDWICK | YO17 6RD | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 132/33kV | 33 | 132 | Melrosegate | OSBALDWICK | YO31 0YB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES | 66 | 132 | North Tees | NORTON | TS23 1PY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE 132/66kV | 66 | 132 | Potter House | SPENNYMOOR | DH1 5FF | ST (DFES) | 89.396 | 88.399 | 87.083 | 86.428 | 85.877 | 84.926 | 83.913 | 82.815 | 82.003 | 80.921 | 77.251 | 72.267 | 67.426 | 63.415 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSWORTH | 66 | 132 | Ravensworth | STELLA SOUTH | DH3 1RQ | ST (DFES) | 76.386 | 76.037 | 75.59 | 75.367 | 75.181 | 74.866 | 74.529 | 74.164 | 73.903 | 73.545 | 72.29 | 70.653 | 69.033 | 67.673 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH GRID | 33 | 132 | Scarborough Grid | OSBALDWICK | YO11 2YH | ST (DFES) | 71.396 | 69.762 | 67.625 | 66.791 | 66.202 | 65.111 | 63.929 | 62.723 | 62.076 | 60.983 | 59.239 | 54.188 | 49.181 | 45.014 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEAL SANDS | 66 | 132 | Seal Sands | SALTHOLME | TS2 1FB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5LJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO | 66 | 132 | Toronto | SPENNYMOOR | DL14 7RJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 3PS | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ATTERCLIFFE | 33 | 132 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3FA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 132/66KV | 66 | 132 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1LR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6NJ | ST (DFES) | 67.4094 | 66.7114 | 65.6354 | 65.1954 | 64.9414 | 64.2244 | 63.4064 | 62.5174 | 61.8654 | 61.0004 | 57.4924 | 52.9794 | 48.8284 | 45.4374 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEVERLEY 132/33KV | 33 | 132 | Beverley 132/33kV | CREYKE BECK | HU17 0RW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 132/33KV | 33 | 132 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | ST (DFES) | 9.9246 | 9.6966 | 9.4096 | 9.1056 | 8.7666 | 8.1786 | 7.5756 | 6.8576 | 6.1376 | 5.3966 | 1.5546 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS B | 33 | 132 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1DA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLYTON | 33 | 132 | Blyton | KEADBY | DN21 3NS | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRADFORD | 33 | 132 | Bradford | BRADFORD WEST | BD1 4RF | ST (DFES) | 99.72 | 99.454 | 99.127 | 98.741 | 98.297 | 97.543 | 96.775 | 95.854 | 94.918 | 93.964 | 88.966 | 84.043 | 79.59 | 75.999 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHAM | 33 | 132 | Bramham | FERRYBRIDGE B | LS24 9NT | ST (DFES) | 26.2347 | 23.4017 | 18.6527 | 17.8217 | 18.3197 | 17.5797 | 16.3057 | 15.3157 | 15.7407 | 14.9877 | 16.8007 | 12.9397 | 8.9057 | 5.3267 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRANSHOLME | 33 | 132 | Bransholme | CREYKE BECK | HU7 4ZN | ST (DFES) | 65.6343 | 65.0233 | 64.0703 | 63.7133 | 63.5333 | 62.9663 | 62.3073 | 61.6033 | 61.1183 | 60.4393 | 57.8223 | 54.2753 | 51.0023 | 48.3223 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | Brighouse 132/33kV | ELLAND | HD6 1PZ | ST (DFES) | 95.8797 | 95.0947 | 93.8597 | 93.4387 | 93.2677 | 92.6177 | 91.8457 | 91.0357 | 90.5277 | 89.7627 | 87.0527 | 83.0057 | 79.2827 | 76.2417 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 8UX | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER CENTRAL | 33 | 132 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1RE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | Driffield/Beverley Group | CREYKE BECK | YO25 5NW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FEATHERSTONE | 33 | 132 | Featherstone | FERRYBRIDGE B | WF7 6HE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIRLINGTON | 33 | 132 | Girlington | BRADFORD WEST | BD7 2NB | ST (DFES) | 85.2785 | 85.1175 | 84.9195 | 84.6865 | 84.4175 | 83.9615 | 83.4975 | 82.9405 | 82.3735 | 81.7965 | 78.7735 | 75.7965 | 73.1035 | 70.9315 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 132/33KV | 33 | 132 | Halifax 132/33kV | ELLAND | HX1 1XB | ST (DFES) | 1.4826 | 1.3936 | 1.2856 | 1.1576 | 1.0136 | 0.76762 | 0.51662 | 0.21662 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HECKMONDWIKE | 33 | 132 | Heckmondwike | SKELTON GRANGE | WF16 9LU | ST (DFES) | 88.836 | 88.65 | 88.422 | 88.153 | 87.844 | 87.321 | 86.789 | 86.15 | 85.5 | 84.837 | 81.353 | 77.945 | 74.854 | 72.358 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLMFIELD | 33 | 132 | Holmfield | BRADFORD WEST | HX2 9AY | ST (DFES) | 57.3035 | 57.0085 | 56.6505 | 56.2265 | 55.7425 | 54.9195 | 54.0825 | 53.0785 | 52.0575 | 51.0185 | 45.5805 | 40.2075 | 35.3555 | 31.4485 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 132/33KV | 33 | 132 | Hull East 132/33kV | SALTEND NORTH | HU9 5NL | ST (DFES) | 8.6907 | 8.4257 | 8.0917 | 7.7087 | 7.2897 | 6.6077 | 5.9057 | 5.0677 | 4.2077 | 3.3057 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL SOUTH | 33 | 132 | Hull South | CREYKE BECK | HU3 5JA | ST (DFES) | 88.4902 | 88.2372 | 87.9272 | 87.5592 | 87.1392 | 86.4342 | 85.7152 | 84.8532 | 83.9732 | 83.0722 | 78.3192 | 73.7272 | 69.5422 | 66.1492 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL WEST | 33 | 132 | Hull West | CREYKE BECK | HU13 0FA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUMBERSTON | 33 | 132 | Humberston | GRIMSBY WEST | DN36 4AW | ST (DFES) | 67.5761 | 67.2711 | 66.8271 | 66.5501 | 66.3091 | 65.8271 | 65.3081 | 64.7141 | 64.1811 | 63.5681 | 60.6221 | 57.5421 | 54.6861 | 52.3431 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNNINGLEY | 33 | 132 | Hunningley | WEST MELTON SECTION 3 | S70 3ET | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNSHELF | 66 | 132 | Hunshelf | WEST MELTON SECTION 3 | S36 8WR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IMMINGHAM | 33 | 132 | Immingham | GRIMSBY WEST | DN40 1QT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKHAW LANE | 33 | 132 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8SB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C 2/5 | 33 | 132 | Kirkstall C 2/5 | KIRKSTALL B | LS18 4EL | ST (DFES) | 81.9512 | 81.8972 | 81.8312 | 81.7532 | 81.6632 | 81.5112 | 81.3562 | 81.1712 | 80.9822 | 80.7882 | 79.7712 | 78.7822 | 77.8822 | 77.1542 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS18 4EL | ST (DFES) | 106.5725 | 106.0735 | 105.3895 | 104.8545 | 104.3225 | 103.3295 | 102.2895 | 101.0735 | 99.9175 | 98.6695 | 92.4505 | 86.0375 | 80.1915 | 75.4505 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS EAST | 33 | 132 | Leeds East | SKELTON GRANGE | LS9 6ED | ST (DFES) | 65.9422 | 65.3862 | 64.5502 | 64.1452 | 63.8542 | 63.1632 | 62.3972 | 61.5442 | 60.8522 | 60.0052 | 56.2802 | 51.8872 | 47.8592 | 44.5782 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS NORTH | 33 | 132 | Leeds North | SKELTON GRANGE | LS7 2AU | ST (DFES) | 107.918 | 107.747 | 107.537 | 107.289 | 107.004 | 106.523 | 106.034 | 105.446 | 104.848 | 104.236 | 101.017 | 97.885 | 95.038 | 92.734 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LINDLEY | 33 | 132 | Lindley | ELLAND | HD3 3NY | ST (DFES) | 92.5802 | 92.0862 | 91.3712 | 90.9392 | 90.5672 | 89.7952 | 88.9662 | 88.0172 | 87.1762 | 86.2192 | 81.7132 | 76.7582 | 72.2402 | 68.5752 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOW ROAD | 33 | 132 | Low Road | SKELTON GRANGE | LS10 1RH | ST (DFES) | 1.732 | 1.561 | 1.336 | 1.126 | 0.90202 | 0.50602 | 0.095016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MALLARD WAY | 33 | 132 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MENSTON | 33 | 132 | Menston | BRADFORD WEST | LS29 6BP | ST (DFES) | 86.9707 | 86.1887 | 84.9297 | 84.5777 | 84.5137 | 84.0147 | 83.3847 | 82.7567 | 82.4627 | 81.8907 | 80.3027 | 77.2607 | 74.4307 | 72.0957 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOSS ROAD | 33 | 132 | Moss Road | GRIMSBY WEST | DN32 0LW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 1/2 | 33 | 132 | Osgodby 1/2 | DRAX | YO8 5HY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 3/4 | 33 | 132 | Osgodby 3/4 | DRAX | YO8 5HY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY | 33 | 132 | Rodley | SKELTON GRANGE | LS13 1PZ | ST (DFES) | 121.6561 | 121.0051 | 120.0061 | 119.5831 | 119.3241 | 118.6261 | 117.8341 | 116.9691 | 116.3181 | 115.4731 | 111.9781 | 107.5681 | 103.5181 | 100.2151 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | ST (DFES) | 81.2678 | 81.0298 | 80.7298 | 80.4068 | 80.0448 | 79.4228 | 78.7858 | 78.0258 | 77.2608 | 76.4718 | 72.3718 | 68.3208 | 64.6438 | 61.6718 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTEND 132/33KV | 33 | 132 | Saltend 132/33kV | SALTEND NORTH | HU12 8EY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SANTON | 33 | 132 | Santon | KEADBY | DN16 1XP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE NORTH | 33 | 132 | Scunthorpe North | KEADBY | DN15 8GN | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE SOUTH | 33 | 132 | Scunthorpe South | KEADBY | DN16 1BD | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILSDEN | 33 | 132 | Silsden | BRADFORD WEST | BD20 0ND | ST (DFES) | 0 | 52.5327 | 50.5367 | 49.7057 | 49.2687 | 48.0307 | 46.6037 | 45.0687 | 43.9597 | 42.4587 | 36.4297 | 28.6257 | 21.4597 | 15.6347 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EL | ST (DFES) | 59.6894 | 59.3344 | 58.8454 | 58.4834 | 58.1364 | 57.4704 | 56.7714 | 55.9554 | 55.1924 | 54.3654 | 50.3084 | 46.0024 | 42.1054 | 38.9624 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAYGATE | 33 | 132 | Staygate | SKELTON GRANGE | BD6 1YA | ST (DFES) | 116.0477 | 115.8347 | 115.5747 | 115.2667 | 114.9137 | 114.3117 | 113.7007 | 112.9667 | 112.2207 | 111.4607 | 107.4777 | 103.5557 | 100.0077 | 97.1457 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNHILL 132KV | 33 | 132 | Thornhill 132kV | ELLAND | WF13 3JQ | ST (DFES) | 19.7347 | 18.8537 | 17.5127 | 16.9157 | 16.5277 | 15.5367 | 14.4227 | 13.1967 | 12.2467 | 11.0367 | 5.8987 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7AL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD NORTH | 33 | 132 | Wakefield North | SKELTON GRANGE | WF1 3HN | ST (DFES) | 80.3254 | 79.2824 | 77.6234 | 77.0854 | 76.8974 | 76.1074 | 75.1484 | 74.1584 | 73.5764 | 72.6304 | 69.3804 | 64.5174 | 59.9494 | 56.1624 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST MELTON | 66 | 132 | West Melton | WEST MELTON SECTION 3 | S63 6EZ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHINMOOR | 33 | 132 | Whinmoor | FERRYBRIDGE B | LS14 2DG | ST (DFES) | 113.5553 | 112.4583 | 110.6963 | 110.1933 | 110.0863 | 109.3633 | 108.4603 | 107.5523 | 107.1073 | 106.2753 | 103.8753 | 99.4623 | 95.3573 | 91.9763 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOLD NEWTON | 33 | 132 | Wold Newton | KEADBY | DN37 0SW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4JJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ACKLAM | 11 | 33 | Bowesfield | NORTON | TS5 7LD | ST (DFES) | 15.7704 | 15.6714 | 15.5594 | 15.4264 | 15.2734 | 15.0184 | 14.7574 | 14.4454 | 14.1364 | 13.8154 | 12.0914 | 10.4984 | 9.0574 | 7.9094 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AMBERTON ROAD | 11 | 66 | Hartmoor | HARTMOOR | TS24 8PQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ANNFIELD 66/20KV | 20 | 66 | Annfield | STELLA SOUTH | DH9 7XW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ASHINGTON | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE63 8UJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE FORREST | 11 | 33 | Darlington North | NORTON | DL1 3NL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | Darlington North | NORTON | DL5 6HY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BARDEN FRIAR | 20 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5JR | ST (DFES) | 7.592 | 7.584 | 7.577 | 7.567 | 7.557 | 7.543 | 7.528 | 7.51 | 7.493 | 7.474 | 7.354 | 7.265 | 7.176 | 7.1 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BEDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 1AH | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BELMONT | 11 | 66 | Potter House | SPENNYMOOR | DH1 2HL | ST (DFES) | 2.8235 | 2.7355 | 2.6425 | 2.5295 | 2.4035 | 2.2015 | 1.9935 | 1.7455 | 1.5025 | 1.2435 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENSHAM | 11 | 66 | Dunston | STELLA NORTH | NE8 2XY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.991 | 11.813 | 11.627 | 10.602 | 9.689 | 8.849 | 8.172 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENTON SQUARE | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE12 9SR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENWELL | 11 | 66 | Dunston | STELLA NORTH | NE4 8XQ | ST (DFES) | 12.124 | 12.04 | 11.956 | 11.855 | 11.74 | 11.55 | 11.357 | 11.125 | 10.9 | 10.664 | 9.356 | 8.178 | 7.101 | 6.234 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | North Tees | NORTON | TS23 2AL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BILLY MILL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE29 8LP | ST (DFES) | 17.3689 | 17.2989 | 17.2229 | 17.1329 | 17.0299 | 16.8569 | 16.6809 | 16.4699 | 16.2629 | 16.0479 | 14.8799 | 13.8049 | 12.8309 | 12.0539 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | ST (DFES) | 32.6472 | 32.5942 | 32.5342 | 32.4632 | 32.3822 | 32.2492 | 32.1122 | 31.9492 | 31.7882 | 31.6192 | 30.7002 | 29.8692 | 29.1102 | 28.5022 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | ST (DFES) | 24.2612 | 24.2262 | 24.1892 | 24.1452 | 24.0952 | 24.0142 | 23.9312 | 23.8322 | 23.7352 | 23.6322 | 23.0572 | 22.5552 | 22.0882 | 21.7102 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLAYDON BURN | 11 | 66 | Dunston | STELLA NORTH | NE21 4BG | ST (DFES) | 1.95 | 1.871 | 1.788 | 1.689 | 1.577 | 1.398 | 1.214 | 0.994 | 0.78 | 0.552 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER 33/11KV | 11 | 33 | Blucher | STELLA NORTH | NE15 9SB | ST (DFES) | 14.5192 | 14.4452 | 14.3662 | 14.2722 | 14.1632 | 13.9802 | 13.7952 | 13.5722 | 13.3532 | 13.1262 | 11.9012 | 10.7652 | 9.7392 | 8.9232 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOLDON DOWNHILL | 20 | 66 | West Boldon | WEST BOLDON | NE36 0AS | ST (DFES) | 19.3145 | 19.2595 | 19.1965 | 19.1215 | 19.0355 | 18.8905 | 18.7445 | 18.5685 | 18.3935 | 18.2135 | 17.2425 | 16.3435 | 15.5325 | 14.8855 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | YO51 9NS | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 33/11KV | 11 | 33 | Bowesfield | NORTON | TS18 3HR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 66/11KV | 11 | 66 | North Tees | NORTON | TS23 1PX | ST (DFES) | 39.3131 | 39.2631 | 39.2111 | 39.1491 | 39.0781 | 38.9661 | 38.8511 | 38.7141 | 38.5811 | 38.4381 | 37.6241 | 36.9331 | 36.2831 | 35.7511 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BRANCEPETH | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL15 0TW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BREAMISH STREET | 11 | 66 | West Boldon | WEST BOLDON | NE1 2BL | ST (DFES) | 22.467 | 22.425 | 22.388 | 22.343 | 22.293 | 22.215 | 22.134 | 22.037 | 21.947 | 21.849 | 21.272 | 20.787 | 20.328 | 19.951 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BRENDA TRADING | 11 | 66 | Hartmoor | HARTMOOR | TS25 1PD | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CAMPLESHON ROAD | 11 | 33 | Melrosegate | OSBALDWICK | YO23 1HZ | ST (DFES) | 0.4187 | 0.3297 | 0.2407 | 0.1357 | 0.015703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARLEY HILL | 11 | 66 | West Boldon | WEST BOLDON | SR5 1SG | ST (DFES) | 19.571 | 19.474 | 19.371 | 19.248 | 19.108 | 18.881 | 18.648 | 18.37 | 18.098 | 17.81 | 16.211 | 14.801 | 13.499 | 12.444 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARLIN HOW T3 T4 | 11 | 66 | Lackenby | LACKENBY | TS13 4DL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARR HILL | 11 | 66 | West Boldon | WEST BOLDON | NE10 9SY | ST (DFES) | 20.0089 | 19.9029 | 19.7839 | 19.6429 | 19.4809 | 19.2139 | 18.9409 | 18.6139 | 18.2909 | 17.9539 | 16.1209 | 14.4569 | 12.9399 | 11.7249 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CATTERICK CAMP | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL9 3HE | ST (DFES) | 8.635 | 8.505 | 8.365 | 8.198 | 8.006 | 7.697 | 7.38 | 7.001 | 6.629 | 6.235 | 4.047 | 2.125 | 0.349 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CLOSE | 11 | 66 | Dunston | STELLA NORTH | NE1 3NB | ST (DFES) | 12.78 | 12.711 | 12.666 | 12.612 | 12.554 | 12.473 | 12.387 | 12.285 | 12.203 | 12.103 | 11.394 | 10.903 | 10.391 | 9.944 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CONEYTHORPE | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG5 0RZ | ST (DFES) | 6.8416 | 6.7746 | 6.7076 | 6.6276 | 6.5366 | 6.3906 | 6.2406 | 6.0626 | 5.8896 | 5.7066 | 4.6626 | 3.7596 | 2.9186 | 2.2336 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CONSETT | 20 | 66 | Annfield | STELLA SOUTH | DH8 7ND | ST (DFES) | 7.744 | 7.61 | 7.464 | 7.29 | 7.091 | 6.772 | 6.443 | 6.051 | 5.666 | 5.258 | 2.987 | 1.002 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CORPORATION STREET | 11 | 33 | Barrack Road | STELLA NORTH | NE4 5SS | ST (DFES) | 19.5775 | 19.5455 | 19.5175 | 19.4835 | 19.4455 | 19.3855 | 19.3225 | 19.2485 | 19.1795 | 19.1055 | 18.6625 | 18.2915 | 17.9395 | 17.6515 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | COWTON | 11 | 33 | Darlington Central | NORTON | DL6 2NF | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLEY | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 2PP | ST (DFES) | 9.512 | 9.479 | 9.448 | 9.411 | 9.37 | 9.308 | 9.243 | 9.165 | 9.093 | 9.012 | 8.532 | 8.146 | 7.773 | 7.463 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 132/6KV | 6 | 132 | Darlington 132/6kV | NORTON | DL1 1SW | ST (DFES) | 0 | 29.7444 | 29.7034 | 29.6534 | 29.5974 | 29.5064 | 29.4134 | 29.3024 | 29.1944 | 29.0794 | 28.4314 | 27.8694 | 27.3464 | 26.9204 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1SW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1HG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON EAST | 11 | 33 | Darlington Central | NORTON | DL1 4NP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON WEST | 11 | 33 | Darlington North | NORTON | DL3 9QG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DENWICK | 20 | 66 | Linton | BLYTH 132kV | NE66 3RG | ST (DFES) | 5.938 | 5.778 | 5.613 | 5.416 | 5.195 | 4.857 | 4.505 | 4.087 | 3.684 | 3.243 | 0.66 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/11KV | 11 | 66 | Dunston | STELLA NORTH | NE11 9DH | ST (DFES) | 1.3623 | 1.3133 | 1.2643 | 1.2043 | 1.1373 | 1.0323 | 0.92428 | 0.79428 | 0.67028 | 0.53528 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/20KV | 20 | 66 | Dunston | STELLA NORTH | NE11 9DH | ST (DFES) | 11.999 | 11.917 | 11.827 | 11.72 | 11.599 | 11.399 | 11.196 | 10.952 | 10.712 | 10.46 | 9.073 | 7.834 | 6.697 | 5.78 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DURHAM EAST | 11 | 66 | Potter House | SPENNYMOOR | DH1 5SU | ST (DFES) | 22.1138 | 22.0648 | 22.0178 | 21.9628 | 21.9018 | 21.8148 | 21.7228 | 21.6138 | 21.5128 | 21.3958 | 20.6628 | 20.1308 | 19.5908 | 19.1248 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EASTFIELD | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 3BY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5129 | 21.2759 | 21.0289 | 19.6659 | 18.4179 | 17.2859 | 16.3819 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EASTGATE CEMENT | 20 | 66 | Toronto | SPENNYMOOR | DL13 2LA | ST (DFES) | 11.654 | 11.624 | 11.594 | 11.559 | 11.52 | 11.461 | 11.401 | 11.328 | 11.26 | 11.183 | 10.719 | 10.361 | 10.009 | 9.711 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | Barrack Road | STELLA NORTH | NE5 4JQ | ST (DFES) | 22.7129 | 22.6589 | 22.6109 | 22.5539 | 22.4889 | 22.3879 | 22.2839 | 22.1589 | 22.0429 | 21.9169 | 21.1719 | 20.5459 | 19.9539 | 19.4679 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ELVINGTON | 11 | 33 | Melrosegate | OSBALDWICK | YO41 4DY | ST (DFES) | 0.9467 | 0.9207 | 0.8987 | 0.8727 | 0.8437 | 0.7997 | 0.7537 | 0.6987 | 0.6487 | 0.5927 | 0.2507 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FARADAY STREET | 11 | 66 | North Tees | NORTON | TS1 4JG | ST (DFES) | 13.2018 | 13.0908 | 12.9798 | 12.8468 | 12.6968 | 12.4578 | 12.2128 | 11.9188 | 11.6368 | 11.3338 | 9.6008 | 8.1238 | 6.7368 | 5.6018 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | Blyth 66kV | BLYTH 66KV | NE3 2SW and NE13 6BH | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FISHBURN | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | TS29 6JQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH CENTRAL | 11 | 33 | Flatworth | TYNEMOUTH | NE29 7SH | ST (DFES) | 30.6847 | 30.6357 | 30.5887 | 30.5327 | 30.4687 | 30.3657 | 30.2597 | 30.1337 | 30.0127 | 29.8837 | 29.1497 | 28.5107 | 27.9177 | 27.4357 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FOSS ISLANDS | 11 | 33 | Melrosegate | OSBALDWICK | YO31 7US | ST (DFES) | 1.3617 | 1.2307 | 1.1217 | 0.9917 | 0.8447 | 0.6167 | 0.3807 | 0.098703 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FOSSWAY 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE6 4AN | ST (DFES) | 14.3839 | 14.2879 | 14.1919 | 14.0769 | 13.9459 | 13.7319 | 13.5129 | 13.2519 | 12.9979 | 12.7319 | 11.2439 | 9.9149 | 8.6939 | 7.7099 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FYLANDS BRIDGE | 11 | 66 | Toronto | SPENNYMOOR | DL14 9TA | ST (DFES) | 9.97 | 9.868 | 9.756 | 9.622 | 9.469 | 9.219 | 8.964 | 8.658 | 8.357 | 8.04 | 6.294 | 4.744 | 3.317 | 2.165 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GALE LANE | 11 | 33 | Poppleton | POPPLETON | YO24 3AF | ST (DFES) | 7.761 | 7.686 | 7.602 | 7.502 | 7.387 | 7.193 | 6.995 | 6.759 | 6.524 | 6.283 | 4.993 | 3.78 | 2.693 | 1.831 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GARWOOD STREET | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 5DQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9026 | 20.6856 | 20.4506 | 19.0696 | 17.9216 | 16.8306 | 15.9316 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD CENTRAL | 11 | 33 | Barrack Road | STELLA NORTH | NE8 1HB | ST (DFES) | 16.9198 | 16.8758 | 16.8338 | 16.7848 | 16.7288 | 16.6458 | 16.5588 | 16.4548 | 16.3568 | 16.2488 | 15.5958 | 15.0828 | 14.5808 | 14.1608 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD EAST | 11 | 66 | West Boldon | WEST BOLDON | NE8 3AH | ST (DFES) | 22.622 | 22.614 | 22.607 | 22.599 | 22.59 | 22.577 | 22.564 | 22.547 | 22.533 | 22.516 | 22.408 | 22.329 | 22.249 | 22.18 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE3 1RR | ST (DFES) | 30.506 | 30.466 | 30.429 | 30.386 | 30.336 | 30.257 | 30.176 | 30.079 | 29.987 | 29.888 | 29.318 | 28.829 | 28.371 | 27.997 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GRANGETOWN | 11 | 66 | Lackenby | LACKENBY | TS6 7AS | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GREATHAM | 11 | 132 | Greatham | SALTHOLME | TS25 2DD | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | Lackenby | LACKENBY | TS14 6GQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARLOW GREEN | 11 | 66 | West Boldon | WEST BOLDON | NE9 6NT | ST (DFES) | 14.4331 | 14.3421 | 14.2391 | 14.1171 | 13.9771 | 13.7461 | 13.5091 | 13.2261 | 12.9461 | 12.6541 | 11.0691 | 9.6271 | 8.3141 | 7.2631 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARMIRE BRIDGE | 20 | 66 | Toronto | SPENNYMOOR | DL12 8QJ | ST (DFES) | 8.339 | 8.256 | 8.173 | 8.074 | 7.964 | 7.797 | 7.624 | 7.418 | 7.221 | 7.003 | 5.703 | 4.678 | 3.68 | 2.842 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARRATON | 11 | 132 | Harraton | STELLA SOUTH | NE38 9BZ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.947 | 36.768 | 36.577 | 35.48 | 34.55 | 33.675 | 32.957 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/11KV | 11 | 132 | Harrogate 132/11kV | KNARESBOROUGH | HG1 2BN | ST (DFES) | 27.663 | 27.481 | 27.297 | 27.077 | 26.827 | 26.428 | 26.017 | 25.527 | 25.052 | 24.547 | 21.68 | 19.202 | 16.892 | 15.013 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE WEST | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 0QB | ST (DFES) | 32.585 | 32.535 | 32.487 | 32.429 | 32.365 | 32.263 | 32.158 | 32.032 | 31.913 | 31.784 | 31.031 | 30.402 | 29.806 | 29.316 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARTMOOR 66/20KV | 20 | 66 | Hartmoor | HARTMOOR | TS27 3BL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HAWTHORN PIT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 9NX | ST (DFES) | 10.446 | 10.314 | 10.169 | 9.996 | 9.799 | 9.476 | 9.146 | 8.752 | 8.362 | 7.954 | 5.706 | 3.7 | 1.858 | 0.374 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | Melrosegate | OSBALDWICK | YO31 8FZ | ST (DFES) | 0.012716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN | 6 | 66 | West Boldon | WEST BOLDON | NE31 1BD | ST (DFES) | 0 | 4.8618 | 4.8418 | 4.8178 | 4.7908 | 4.7488 | 4.7058 | 4.6538 | 4.6048 | 4.5518 | 4.2428 | 3.9828 | 3.7368 | 3.5358 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN WEST | 11 | 66 | West Boldon | WEST BOLDON | NE31 1NA | ST (DFES) | 0.0056837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEDWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE32 4SW | ST (DFES) | 0.38429 | 0.32929 | 0.26929 | 0.19729 | 0.11429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEIGHINGTON | 11 | 33 | Darlington North | NORTON | DL5 6JW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEXHAM | 20 | 66 | Coalburns | STELLA SOUTH | NE46 4NT | ST (DFES) | 28.0169 | 27.9449 | 27.8679 | 27.7769 | 27.6729 | 27.5089 | 27.3399 | 27.1389 | 26.9419 | 26.7309 | 25.5319 | 24.5169 | 23.5619 | 22.7799 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HIGH BARMSTON | 11 | 66 | West Boldon | WEST BOLDON | NE38 8QA | ST (DFES) | 20.754 | 20.686 | 20.616 | 20.532 | 20.436 | 20.284 | 20.127 | 19.94 | 19.758 | 19.564 | 18.471 | 17.525 | 16.643 | 15.925 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HIGH FLATTS | 11 | 66 | Potter House | SPENNYMOOR | DH2 2LR | ST (DFES) | 21.3672 | 21.2682 | 21.1572 | 21.0252 | 20.8752 | 20.6312 | 20.3802 | 20.0812 | 19.7862 | 19.4752 | 17.7612 | 16.2422 | 14.8422 | 13.7122 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HOUGHTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | DH4 5HP | ST (DFES) | 3.8291 | 3.7441 | 3.6521 | 3.5411 | 3.4141 | 3.2081 | 2.9961 | 2.7431 | 2.4931 | 2.2321 | 0.79314 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HOWDON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 0JX | ST (DFES) | 4.3515 | 4.3265 | 4.3025 | 4.2725 | 4.2385 | 4.1825 | 4.1255 | 4.0575 | 3.9905 | 3.9215 | 3.5355 | 3.1885 | 2.8705 | 2.6155 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUNTINGTON NEW LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO32 9TA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | Husthwaite | KNARESBOROUGH | YO61 4PN | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | JARROW | 11 | 33 | South Shields | SOUTH SHIELDS | NE32 5LD | ST (DFES) | 18.4196 | 18.3986 | 18.3766 | 18.3516 | 18.3226 | 18.2766 | 18.2286 | 18.1726 | 18.1176 | 18.0596 | 17.7276 | 17.4416 | 17.1746 | 16.9566 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KENTON | 11 | 33 | Blucher | STELLA NORTH | NE3 4UP | ST (DFES) | 3.2091 | 3.1461 | 3.0801 | 3.0001 | 2.9091 | 2.7581 | 2.6031 | 2.4181 | 2.2371 | 2.0481 | 1.0201 | 0.076103 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KIELDER | 20 | 33 | Spadeadam 33kV | SPADEADAM | NE48 1BH | ST (DFES) | 4.056 | 4.048 | 4.04 | 4.031 | 4.02 | 4.005 | 3.99 | 3.971 | 3.954 | 3.934 | 3.809 | 3.719 | 3.626 | 3.547 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KILLINGWORTH | 11 | 33 | Gosforth | TYNEMOUTH | NE12 6QQ | ST (DFES) | 11.599 | 11.542 | 11.481 | 11.409 | 11.325 | 11.187 | 11.046 | 10.876 | 10.71 | 10.538 | 9.595 | 8.733 | 7.95 | 7.324 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KIRBYMOORSIDE | 11 | 66 | Malton Grid | OSBALDWICK | YO62 6EZ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LINTON 66/20KV | 20 | 66 | Linton | BLYTH 132kV | NE61 3AX | ST (DFES) | 7.384 | 7.326 | 7.262 | 7.187 | 7.1 | 6.96 | 6.817 | 6.646 | 6.477 | 6.299 | 5.308 | 4.441 | 3.638 | 2.987 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LONGBENTON | 11 | 33 | Gosforth | TYNEMOUTH | NE7 7LR | ST (DFES) | 19.5882 | 19.5142 | 19.4362 | 19.3442 | 19.2372 | 19.0602 | 18.8792 | 18.6632 | 18.4502 | 18.2302 | 17.0272 | 15.9232 | 14.9222 | 14.1222 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LOW SPENNYMOOR | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL16 7RS | ST (DFES) | 8.026 | 7.968 | 7.902 | 7.824 | 7.734 | 7.587 | 7.438 | 7.258 | 7.081 | 6.895 | 5.877 | 4.965 | 4.129 | 3.456 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LYNEMOUTH | 20 | 66 | Linton | BLYTH 132kV | NE61 5XH | ST (DFES) | 6.078 | 6.064 | 6.049 | 6.03 | 6.009 | 5.974 | 5.938 | 5.895 | 5.853 | 5.809 | 5.568 | 5.349 | 5.15 | 4.991 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MADDISON STREET | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE24 1HD | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALLEABLE | 11 | 66 | North Tees | NORTON | TS18 2NR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7269 | 1.5629 | 1.3829 | 0.31688 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALTON | 11 | 66 | Malton Grid | OSBALDWICK | YO17 6BT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MEADOWFIELD | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH7 8ER | ST (DFES) | 0.903 | 0.868 | 0.831 | 0.787 | 0.738 | 0.661 | 0.582 | 0.488 | 0.397 | 0.298 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 33/11KV | 11 | 33 | Melrosegate | OSBALDWICK | YO31 0YB | ST (DFES) | 1.6767 | 1.6237 | 1.5717 | 1.5097 | 1.4387 | 1.3227 | 1.2037 | 1.0617 | 0.9247 | 0.7807 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MILLBANK LANE | 11 | 33 | Bowesfield | NORTON | TS17 0AX | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.2212 | 18.9782 | 18.7252 | 17.3522 | 16.1032 | 14.9662 | 14.0562 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MONKSEATON | 11 | 33 | Chirton Grange | TYNEMOUTH | NE25 9AF | ST (DFES) | 19.4492 | 19.3322 | 19.2112 | 19.0672 | 18.9032 | 18.6342 | 37.598 | 37.269 | 36.949 | 36.612 | 34.742 | 33.071 | 31.537 | 30.301 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MOOR MONKTON PUMPS | 11 | 33 | Poppleton | POPPLETON | YO30 1BY | ST (DFES) | 13.4109 | 13.3999 | 13.3879 | 13.3729 | 13.3569 | 13.3309 | 13.3039 | 13.2719 | 13.2409 | 13.2079 | 13.0209 | 12.8599 | 12.7099 | 12.5869 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MORPETH | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE61 6JH | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MOUNT ROAD | 11 | 33 | Offerton | OFFERTON | SR4 7LJ | ST (DFES) | 24.1092 | 24.0122 | 23.9132 | 23.7952 | 23.6622 | 23.4512 | 23.2342 | 22.9742 | 22.7232 | 22.4542 | 20.9162 | 19.6092 | 18.3802 | 17.3742 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWBURN HAUGH | 11 | 132 | Newburn Haugh | STELLA NORTH | NE15 8SF | ST (DFES) | 20.4544 | 20.4264 | 20.3974 | 20.3624 | 20.3224 | 20.2574 | 20.1904 | 20.1104 | 20.0334 | 19.9514 | 19.5014 | 19.0954 | 18.7244 | 18.4264 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWBY | 11 | 33 | Scarborough Grid | OSBALDWICK | YO12 6NL | ST (DFES) | 0.22287 | 0.15187 | 0.076868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWCASTLE AIRPORT | 11 | 33 | Blucher | STELLA NORTH | NE13 8DF | ST (DFES) | 27.1413 | 27.0923 | 27.0363 | 26.9703 | 26.8943 | 26.7693 | 26.6413 | 26.4883 | 26.3363 | 26.1783 | 25.3203 | 24.5383 | 23.8273 | 23.2593 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | Darlington North | NORTON | DL5 6EA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH STREET | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 1DU | ST (DFES) | 1.4274 | 1.3364 | 1.2664 | 1.1834 | 1.0894 | 0.9454 | 0.7964 | 0.6184 | 0.4604 | 0.2854 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T1 T2 | 11 | 66 | North Tees | NORTON | TS23 1PX | ST (DFES) | 22.3514 | 22.3104 | 22.2794 | 22.2414 | 22.2014 | 22.1524 | 22.0984 | 22.0344 | 21.9814 | 21.9134 | 21.4144 | 21.1174 | 20.7814 | 20.4734 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T3 T4 | 11 | 66 | North Tees | NORTON | TS23 1PY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6077 | 8.4817 | 8.3397 | 7.4707 | 6.8067 | 6.1497 | 5.5917 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTHALLERTON | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 0QE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTON 132/11KV | 11 | 132 | Norton 132/11kV | NORTON | TS21 1EG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | OATLANDS | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 8BY | ST (DFES) | 18.3108 | 18.2468 | 18.1788 | 18.0988 | 18.0068 | 17.8578 | 17.7048 | 17.5228 | 17.3438 | 17.1558 | 16.1108 | 15.1828 | 14.3288 | 13.6398 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | OFFERTON 33/11KV | 11 | 33 | Offerton | OFFERTON | SR4 9NR | ST (DFES) | 26.6068 | 26.5218 | 26.4248 | 26.3098 | 26.1778 | 25.9578 | 25.7338 | 25.4648 | 25.1978 | 24.9218 | 23.4298 | 22.0588 | 20.8158 | 19.8238 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PALLION TRADING | 11 | 33 | Offerton | OFFERTON | SR4 6SN | ST (DFES) | 13.6258 | 13.5458 | 13.4628 | 13.3628 | 13.2508 | 13.0698 | 12.8848 | 12.6628 | 12.4478 | 12.2188 | 10.9238 | 9.8058 | 8.7628 | 7.9128 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2HR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE WEST | 11 | 66 | Hartmoor | HARTMOOR | DH6 2RA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PILGRIM | 11 | 33 | Barrack Road | STELLA NORTH | NE1 2LA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7682 | 3.7402 | 3.7022 | 3.4072 | 3.2282 | 3.0272 | 2.8452 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | Potter House | SPENNYMOOR | DH1 5FF | ST (DFES) | 4.537 | 4.43 | 4.31 | 4.167 | 4.002 | 3.733 | 3.457 | 3.127 | 2.8 | 2.459 | 0.59505 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | Potter House | SPENNYMOOR | DH1 5FF | ST (DFES) | 26.2342 | 26.2152 | 26.1952 | 26.1712 | 26.1452 | 26.1042 | 26.0622 | 26.0122 | 25.9642 | 25.9122 | 25.6022 | 25.3532 | 25.1122 | 24.9122 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PRISSICK | 11 | 66 | Lackenby | LACKENBY | TS4 3SG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSCAR | 11 | 33 | Scarborough Grid | OSBALDWICK | YO13 0LZ | ST (DFES) | 10.024 | 10.014 | 10.005 | 9.995 | 9.984 | 9.967 | 9.949 | 9.928 | 9.909 | 9.888 | 9.759 | 9.653 | 9.552 | 9.468 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAWCLIFFE LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO30 5SW | ST (DFES) | 0.8727 | 0.7947 | 0.7177 | 0.6267 | 0.5217 | 0.3517 | 0.1777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | REDCAR | 11 | 66 | Lackenby | LACKENBY | TS10 2PA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RESERVOIR | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE22 5QP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T1 | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL10 5BJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T2 | 11 | 33 | Darlington North | NORTON | DL10 5BJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RIPON | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG4 1QE | ST (DFES) | 14.4159 | 14.2909 | 14.1689 | 17.981 | 17.817 | 17.558 | 17.292 | 16.974 | 16.67 | 16.342 | 14.442 | 12.844 | 11.335 | 10.096 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RISE CARR | 6 | 33 | Darlington North | NORTON | DL3 0RP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ROMANBY | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 8HP | ST (DFES) | 9.9811 | 9.9381 | 9.8871 | 9.8261 | 9.7551 | 9.6381 | 9.5171 | 9.3741 | 9.2301 | 9.0811 | 8.2891 | 7.5531 | 6.8901 | 6.3641 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RUDBY | 11 | 33 | Bowesfield | NORTON | TS15 0JT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 2YH | ST (DFES) | 2.21 | 2.084 | 1.973 | 1.839 | 1.687 | 1.442 | 1.191 | 0.89002 | 0.60902 | 0.30802 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEGHILL | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 7EY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | Husthwaite | KNARESBOROUGH | YO7 3NT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEVERUS HILL | 11 | 33 | Poppleton | POPPLETON | YO26 4RR | ST (DFES) | 0.78357 | 0.71157 | 0.64057 | 0.55557 | 0.45757 | 0.29757 | 0.13457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SHERIFF HUTTON | 11 | 66 | Malton Grid | OSBALDWICK | YO60 6QN | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SHOTTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2EL | ST (DFES) | 1.3682 | 1.2992 | 1.2242 | 1.1342 | 1.0312 | 0.86517 | 0.69517 | 0.49117 | 0.29117 | 0.080169 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SIMONSIDE | 11 | 33 | South Shields | SOUTH SHIELDS | NE34 9PD | ST (DFES) | 13.2181 | 13.1631 | 13.1051 | 13.0351 | 12.9551 | 12.8241 | 12.6911 | 12.5301 | 12.3741 | 12.2101 | 11.3051 | 10.4911 | 9.7461 | 9.1471 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SKELDERGATE | 11 | 33 | Poppleton | POPPLETON | YO1 6HN | ST (DFES) | 2.1169 | 2.0599 | 2.0169 | 1.9659 | 1.9089 | 1.8259 | 1.7379 | 1.6339 | 1.5439 | 1.4399 | 0.77088 | 0.25888 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SKERNESIDE | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL5 6JH | ST (DFES) | 0.30662 | 0.21562 | 0.12062 | 0.0076182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENCERBECK | 11 | 66 | Lackenby | LACKENBY | TS3 8TE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5JX | ST (DFES) | 0.74067 | 0.65067 | 0.55367 | 0.43667 | 0.30467 | 0.090669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STARBECK | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 7PT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STOKESLEY | 11 | 33 | Bowesfield | NORTON | TS9 5HS | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STONEY CUT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 8RQ | ST (DFES) | 15.8952 | 15.8092 | 15.7132 | 15.5992 | 15.4692 | 15.2572 | 15.0392 | 14.7802 | 14.5242 | 14.2542 | 12.7702 | 11.4512 | 10.2372 | 9.2582 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T1 T2 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | ST (DFES) | 21.0423 | 20.9553 | 20.8763 | 20.7823 | 20.6783 | 20.5253 | 20.3653 | 20.1753 | 19.9993 | 19.8003 | 18.5633 | 17.6273 | 16.6963 | 15.9043 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T5 T6 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | ST (DFES) | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.799 | 22.799 | 22.799 | 22.799 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TANFIELD | 11 | 66 | Annfield | STELLA SOUTH | DH9 9DB | ST (DFES) | 0.60715 | 0.52815 | 0.44015 | 0.33415 | 0.21415 | 0.01715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEAM VALLEY | 20 | 66 | Ravensworth | STELLA SOUTH | NE11 0SX | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.1431 | 45.0721 | 44.9851 | 44.4041 | 44.0171 | 43.6051 | 43.2411 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | Seal Sands | SALTHOLME | TS23 3NF | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEMPLE PARK | 11 | 66 | West Boldon | WEST BOLDON | NE34 8TH | ST (DFES) | 20.0894 | 20.0014 | 19.9034 | 19.7874 | 19.6534 | 19.4304 | 19.2034 | 18.9314 | 18.6624 | 18.3834 | 16.8754 | 15.4854 | 14.2274 | 13.2244 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | THIRSK | 11 | 33 | Leeming Bar_Skeeby | NORTON | YO7 4NH | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | THORNTON DALE | 11 | 66 | Malton Grid | OSBALDWICK | YO18 7SJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO 66/20KV | 20 | 66 | Toronto | SPENNYMOOR | DL14 7RJ | ST (DFES) | 8.173 | 8.062 | 7.947 | 7.808 | 7.652 | 7.406 | 7.152 | 6.849 | 6.555 | 6.238 | 4.429 | 2.907 | 1.47 | 0.289 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TUNSTALL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR3 2BT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.0049 | 25.6829 | 25.3499 | 23.5459 | 21.8909 | 20.3909 | 19.1919 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE30 1JG | ST (DFES) | 19.7225 | 19.6195 | 19.5205 | 19.4015 | 19.2675 | 19.0545 | 18.8345 | 18.5715 | 18.3215 | 18.0535 | 16.5125 | 15.1885 | 13.9505 | 12.9405 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | UNIVERSITY | 11 | 33 | Barrack Road | STELLA NORTH | NE2 4PZ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5777 | 10.5267 | 10.4697 | 10.1107 | 9.8297 | 9.5557 | 9.3237 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | URLAY NOOK | 11 | 33 | Bowesfield | NORTON | TS16 0QB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | USWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE37 3HY | ST (DFES) | 21.62 | 21.582 | 21.541 | 21.493 | 21.437 | 21.347 | 21.255 | 21.144 | 21.036 | 20.922 | 20.289 | 19.73 | 19.213 | 18.796 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WALKER | 11 | 66 | West Boldon | WEST BOLDON | NE6 3PZ | ST (DFES) | 14.6309 | 14.5469 | 14.4619 | 14.3589 | 14.2419 | 14.0489 | 13.8519 | 13.6159 | 13.3859 | 13.1459 | 11.8159 | 10.6159 | 9.5199 | 8.6389 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WANSBECK | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE22 7DH | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WARDLEY | 6 | 66 | West Boldon | WEST BOLDON | NE31 1LP | ST (DFES) | 0 | 15.7294 | 15.6814 | 15.6234 | 15.5584 | 15.4504 | 15.3394 | 15.2074 | 15.0764 | 14.9404 | 14.1924 | 13.5194 | 12.9034 | 12.4084 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WARKWORTH | 20 | 66 | Linton | BLYTH 132kV | NE65 0YD | ST (DFES) | 6.432 | 6.312 | 6.186 | 6.034 | 5.863 | 5.593 | 5.314 | 4.982 | 4.659 | 4.311 | 2.329 | 0.657 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WENSLEYDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5ED | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST HARTFORD | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 3JP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST SOUTHWICK | 11 | 66 | West Boldon | WEST BOLDON | SR5 3TX | ST (DFES) | 20.656 | 20.609 | 20.557 | 20.496 | 20.427 | 20.314 | 20.198 | 20.059 | 19.924 | 19.781 | 18.987 | 18.285 | 17.637 | 17.114 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST WYLAM | 20 | 66 | Coalburns | STELLA SOUTH | NE42 5EX | ST (DFES) | 0.22836 | 0.10836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WESTERHOPE | 11 | 33 | Blucher | STELLA NORTH | NE5 5HH | ST (DFES) | 19.0703 | 19.0053 | 18.9333 | 18.8483 | 18.7503 | 18.5853 | 18.4173 | 18.2163 | 18.0173 | 17.8123 | 16.7073 | 15.6793 | 14.7523 | 14.0153 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WESTOE | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 3GE | ST (DFES) | 13.182 | 13.109 | 13.032 | 12.939 | 12.834 | 12.661 | 12.484 | 12.272 | 12.065 | 11.848 | 10.648 | 9.573 | 8.587 | 7.793 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO22 4JE | ST (DFES) | 11.7951 | 11.7671 | 11.7441 | 11.7171 | 11.6871 | 11.6391 | 11.5891 | 11.5301 | 11.4761 | 11.4181 | 11.0651 | 10.7681 | 10.4881 | 10.2571 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO22 4JE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO21 1LY | ST (DFES) | 11.7179 | 11.6869 | 11.6589 | 11.6259 | 11.5879 | 11.5279 | 11.4649 | 11.3909 | 11.3209 | 11.2459 | 10.8149 | 10.4379 | 10.0889 | 9.8049 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO21 1LY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WILLINGTON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 7HS | ST (DFES) | 18.5612 | 18.4902 | 18.4132 | 18.3212 | 18.2152 | 18.0372 | 17.8562 | 17.6392 | 17.4252 | 17.2032 | 16.0092 | 14.9012 | 13.9012 | 13.1062 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | Wormald Green 132/11kV | KNARESBOROUGH | HG3 3PS | ST (DFES) | 13.151 | 13.094 | 13.037 | 12.969 | 12.891 | 12.769 | 12.643 | 12.492 | 12.347 | 12.192 | 11.304 | 10.544 | 9.833 | 9.252 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WYNYARD | 11 | 66 | Hartmoor | HARTMOOR | TS2 2FB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | YEDINGHAM | 11 | 66 | Malton Grid | OSBALDWICK | YO17 8RR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | YORK UNIVERSITY | 11 | 33 | Melrosegate | OSBALDWICK | YO10 5ZF | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ABBEY ROAD | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS5 3NF | ST (DFES) | 1.8593 | 1.8233 | 1.7783 | 1.7253 | 1.6643 | 1.5623 | 1.4573 | 1.3323 | 1.2053 | 1.0743 | 0.38833 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AIREDALE ROAD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 4LJ | ST (DFES) | 13.0766 | 13.0506 | 13.0176 | 12.9786 | 12.9336 | 12.8576 | 12.7806 | 12.6876 | 12.5936 | 12.4966 | 11.9936 | 11.4976 | 11.0486 | 10.6866 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALDHAM | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S73 8SW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALFRED GELDER STREET | 11 | 33 | Hull South | CREYKE BECK | HU1 1EP | ST (DFES) | 2.8759 | 2.8609 | 2.8439 | 2.8229 | 2.7989 | 2.7569 | 2.7159 | 2.6649 | 2.6139 | 2.5619 | 2.2899 | 2.0209 | 1.7779 | 1.5819 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T1 | 11 | 33 | Leeds East | SKELTON GRANGE | LS7 3QB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T2 | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 3QB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALVERTHORPE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 9PB | ST (DFES) | 21.6773 | 21.6093 | 21.5243 | 21.4223 | 21.3073 | 21.1193 | 20.9263 | 20.6963 | 20.4593 | 20.2123 | 18.8953 | 17.6763 | 16.5443 | 15.6163 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARMOURIES DRIVE | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LT | ST (DFES) | 7.111 | 7.094 | 7.073 | 7.049 | 7.02 | 6.972 | 6.923 | 6.865 | 6.805 | 6.744 | 6.423 | 6.111 | 5.827 | 5.597 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARMTHORPE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3DY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARUNDEL STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4PJ | ST (DFES) | 4.4338 | 4.4248 | 4.4128 | 4.3998 | 4.3848 | 4.3588 | 4.3318 | 4.3008 | 4.2688 | 4.2358 | 4.0638 | 3.8948 | 3.7408 | 3.6178 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ASKERN | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN6 0BY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AUDBY LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 7SU | ST (DFES) | 3.5604 | 3.5064 | 3.4374 | 3.3544 | 3.2634 | 3.1204 | 2.9714 | 2.7954 | 2.6114 | 2.4144 | 1.3434 | 0.42238 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AUSTERFIELD | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN10 6HD | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BAILIFF BRIDGE | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 4DT | ST (DFES) | 1.2995 | 1.2615 | 1.2155 | 1.1615 | 1.1005 | 0.99548 | 0.88848 | 0.76148 | 0.63148 | 0.49848 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BALBY | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN4 8DG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BALME STREET | 11 | 33 | Bradford | BRADFORD WEST | BD1 4BA | ST (DFES) | 3.3196 | 3.2926 | 3.2606 | 3.2216 | 3.1776 | 3.1026 | 3.0256 | 2.9346 | 2.8406 | 2.7456 | 2.2476 | 1.7576 | 1.3136 | 0.9556 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNBURGH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 9NT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNOLDSWICK | 11 | 33 | Silsden | BRADFORD WEST | BB18 5RU | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 7AU | ST (DFES) | 32.1582 | 32.1322 | 32.1002 | 32.0622 | 32.0192 | 31.9452 | 31.8702 | 31.7792 | 31.6882 | 31.5952 | 31.1062 | 30.6242 | 30.1882 | 29.8372 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARROW | 11 | 33 | Immingham | GRIMSBY WEST | DN19 7EG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 66/11KV | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1HT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARWICK | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS15 8SW | ST (DFES) | 13.1094 | 13.0614 | 13.0024 | 12.9324 | 12.8524 | 12.7174 | 12.5794 | 12.4154 | 12.2464 | 12.0754 | 11.1714 | 10.2914 | 9.4914 | 8.8444 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BASLOW ROAD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S17 3LT | ST (DFES) | 0.22592 | 0.18592 | 0.13792 | 0.079919 | 0.013919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BATLEY | 11 | 33 | Thornhill 132kV | ELLAND | WF17 6HU | ST (DFES) | 4.8554 | 4.7894 | 4.7084 | 4.6134 | 4.5044 | 4.3194 | 4.1314 | 3.9054 | 3.6764 | 3.4414 | 2.2104 | 1.0054 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEAL | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8DT | ST (DFES) | 3.9061 | 3.8751 | 3.8351 | 3.7881 | 3.7371 | 3.6571 | 3.5741 | 3.4751 | 3.3721 | 3.2631 | 2.6711 | 2.1521 | 1.6601 | 1.2511 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | ST (DFES) | 8.5735 | 8.5595 | 8.5415 | 8.5205 | 8.4965 | 8.4565 | 8.4155 | 8.3665 | 8.3155 | 8.2645 | 7.9945 | 7.7315 | 7.4925 | 7.2995 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | ST (DFES) | 38.4242 | 38.3902 | 38.3482 | 38.2992 | 38.2422 | 38.1472 | 38.0492 | 37.9332 | 37.8142 | 37.6922 | 37.0522 | 36.4302 | 35.8642 | 35.4062 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEIGHTON | 11 | 66 | Thurcroft | THURCROFT | S26 4TL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELLHOUSE ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 0PL | ST (DFES) | 1.3247 | 1.2607 | 1.1817 | 1.0887 | 0.98173 | 0.79973 | 0.61473 | 0.39273 | 0.16673 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT AVENUE | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DF | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT COVERT | 11 | 33 | Wold Newton | KEADBY | LN11 9RA | ST (DFES) | 0.024462 | 0.018462 | 0.010462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELTHORPE LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1SB | ST (DFES) | 12.337 | 12.327 | 12.313 | 12.298 | 12.281 | 12.255 | 12.229 | 12.197 | 12.163 | 12.128 | 11.932 | 11.766 | 11.607 | 11.473 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BENTLEY | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN5 0NG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BILLET LANE | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINBROOK | 11 | 33 | Wold Newton | KEADBY | LN8 6DR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 33/11KV | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | ST (DFES) | 13.4026 | 13.3546 | 13.2946 | 13.2246 | 13.1436 | 13.0056 | 12.8666 | 12.6986 | 12.5286 | 12.3546 | 11.4426 | 10.5476 | 9.7366 | 9.0816 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BIRKBY | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 5HB | ST (DFES) | 0.27955 | 0.22855 | 0.16655 | 0.093548 | 0.0095485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1HF | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLUE BOY STREET | 11 | 33 | Neepsend | NEEPSEND | S3 7BA | ST (DFES) | 1.36 | 1.35 | 1.337 | 1.323 | 1.306 | 1.278 | 1.249 | 1.214 | 1.179 | 1.143 | 0.95596 | 0.77096 | 0.60396 | 0.46896 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOC BRINSWORTH | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1WT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOLTON ROAD | 11 | 33 | Silsden | BRADFORD WEST | BD20 0JT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOTTESFORD | 11 | 33 | Scunthorpe South | KEADBY | DN16 3UJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHOPE | 11 | 33 | Menston | BRADFORD WEST | LS16 9HA | ST (DFES) | 0.75111 | 0.73911 | 0.72511 | 0.70711 | 0.68811 | 0.65411 | 0.62011 | 0.57911 | 0.53711 | 0.49411 | 0.27011 | 0.05111 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMLEY | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS13 3ST | ST (DFES) | 21.6308 | 21.5648 | 21.4828 | 21.3868 | 21.2758 | 21.0898 | 20.8998 | 20.6718 | 20.4388 | 20.2018 | 18.9528 | 17.7368 | 16.6318 | 15.7378 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRETT STREET | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 4HW | ST (DFES) | 17.1475 | 17.0185 | 16.8565 | 16.6655 | 16.4595 | 16.1345 | 15.7985 | 15.3985 | 14.9825 | 14.5425 | 12.1515 | 10.0545 | 8.0685 | 6.4185 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIDGES ROAD | 11 | 33 | Scunthorpe South | KEADBY | DN17 1HA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1QE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRODSWORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 7XB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BROOKFIELD STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LD | ST (DFES) | 2.5369 | 2.5349 | 2.5329 | 2.5299 | 2.5269 | 2.5219 | 2.5169 | 2.5109 | 2.5049 | 2.4989 | 2.4659 | 2.4339 | 2.4039 | 2.3809 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BTP | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN31 2RL | ST (DFES) | 16.3847 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3827 | 16.3817 | 16.3807 | 16.3807 | 16.3797 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURLEY STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS3 1JY | ST (DFES) | 39.9961 | 39.9771 | 39.9541 | 39.9261 | 39.8941 | 39.8411 | 39.7861 | 39.7211 | 39.6541 | 39.5861 | 39.2271 | 38.8791 | 38.5621 | 38.3051 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURMANTOFTS | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 7SS | ST (DFES) | 10.3155 | 10.3005 | 10.2825 | 10.2605 | 10.2355 | 10.1925 | 10.1495 | 10.0975 | 10.0445 | 9.9905 | 9.7075 | 9.4305 | 9.1795 | 8.9765 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURNLEYVILLE | 11 | 33 | Heckmondwike | SKELTON GRANGE | BD19 4RY | ST (DFES) | 1.8764 | 1.8254 | 1.7624 | 1.6874 | 1.6024 | 1.4574 | 1.3104 | 1.1334 | 0.9534 | 0.7704 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURTON PIDSEA | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU12 9AE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURTON ROAD | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 2QG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 2HG | ST (DFES) | 10.8143 | 10.7673 | 10.7093 | 10.6413 | 10.5633 | 10.4303 | 10.2963 | 10.1353 | 9.9703 | 9.8023 | 8.9173 | 8.0573 | 7.2743 | 6.6413 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BUTTERWICK | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO17 8HF | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CAISTOR | 11 | 33 | Wold Newton | KEADBY | LN7 6RE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CALDER WHARF | 11 | 33 | Thornhill 132kV | ELLAND | WF13 3JQ | ST (DFES) | 19.9058 | 19.8508 | 19.7828 | 19.7018 | 19.6098 | 19.4548 | 19.2968 | 19.1068 | 18.9138 | 18.7158 | 17.6778 | 16.6648 | 15.7448 | 15.0018 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CARLTON HILL | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 1JB | ST (DFES) | 22.2124 | 22.1914 | 22.1664 | 22.1364 | 22.1024 | 22.0444 | 21.9844 | 21.9144 | 21.8414 | 21.7674 | 21.3794 | 21.0004 | 20.6564 | 20.3784 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CARR LANE | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 4PS | ST (DFES) | 22.4597 | 22.4147 | 22.3577 | 22.2897 | 22.2137 | 22.0887 | 21.9597 | 21.8067 | 21.6487 | 21.4847 | 20.6087 | 19.7977 | 19.0447 | 18.4267 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CHELKER RESERVOIR | 11 | 33 | Silsden | BRADFORD WEST | LS29 0JS | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CHEVIN END | 11 | 33 | Menston | BRADFORD WEST | LS29 6BE | ST (DFES) | 23.4135 | 23.3815 | 23.3425 | 23.2955 | 23.2425 | 23.1515 | 23.0585 | 22.9475 | 22.8345 | 22.7195 | 22.1165 | 21.5235 | 20.9865 | 20.5535 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENCE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1JE | ST (DFES) | 7.635 | 7.623 | 7.609 | 7.592 | 7.573 | 7.54 | 7.507 | 7.467 | 7.426 | 7.385 | 7.166 | 6.952 | 6.759 | 6.602 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON ROAD | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS2 9JT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON STREET | 11 | 33 | Hull South | CREYKE BECK | HU3 1AP | ST (DFES) | 22.2799 | 22.2529 | 22.2209 | 22.1829 | 22.1389 | 22.0629 | 21.9859 | 21.8939 | 21.7999 | 21.7049 | 21.2059 | 20.7119 | 20.2659 | 19.9069 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLAYWHEELS LANE | 11 | 33 | Neepsend | NEEPSEND | S6 1LY | ST (DFES) | 22.6391 | 22.5541 | 22.4511 | 22.3301 | 22.1891 | 21.9501 | 21.7071 | 21.4161 | 21.1191 | 20.8181 | 19.2391 | 17.6801 | 16.2711 | 15.1361 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLOUGH LANE | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3EH | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COMMONSIDE LANE | 11 | 33 | Featherstone | FERRYBRIDGE B | WF7 5DF | ST (DFES) | 5.3588 | 5.3178 | 5.2668 | 5.9068 | 5.8388 | 5.7268 | 5.6118 | 5.4738 | 5.3328 | 5.1858 | 4.4018 | 3.6758 | 3.0018 | 2.4498 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CONVAMORE ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN32 9PG | ST (DFES) | 14.0623 | 14.0173 | 13.9603 | 13.8933 | 13.8173 | 13.6913 | 13.5623 | 13.4073 | 13.2493 | 13.0853 | 12.2143 | 11.3973 | 10.6423 | 10.0263 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CONYARD ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN35 7LQ | ST (DFES) | 10.7346 | 10.6736 | 10.5986 | 10.5086 | 10.4066 | 10.2386 | 10.0676 | 9.8616 | 9.6506 | 9.4326 | 8.2716 | 7.1816 | 6.1766 | 5.3546 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CORNWALL STREET | 11 | 132 | Cornwall Street | CREYKE BECK | HU8 8AQ | ST (DFES) | 32.4377 | 32.4117 | 32.3807 | 32.3437 | 32.3007 | 32.2277 | 32.1537 | 32.0637 | 31.9737 | 31.8817 | 31.3987 | 30.9217 | 30.4907 | 30.1437 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CORRINGHAM ROAD | 11 | 33 | Blyton | KEADBY | DN21 1FT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COSTHORPE | 11 | 66 | Thurcroft | THURCROFT | S81 9QR | ST (DFES) | 6.6661 | 6.6411 | 6.6071 | 6.5681 | 6.5251 | 6.4631 | 6.3981 | 6.3201 | 6.2381 | 6.1471 | 5.6381 | 5.2431 | 4.8471 | 4.5061 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COUNTY ROAD NORTH | 11 | 33 | Hull South | CREYKE BECK | HU5 5DR | ST (DFES) | 8.2924 | 8.1934 | 8.0704 | 7.9264 | 7.7624 | 7.4904 | 7.2114 | 6.8784 | 6.5374 | 6.1864 | 4.3244 | 2.5554 | 0.9314 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CRACOE | 11 | 33 | Silsden | BRADFORD WEST | BD23 6BE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROOKESMOOR ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 3FP | ST (DFES) | 3.5737 | 3.5057 | 3.4237 | 3.3257 | 3.2127 | 3.0217 | 2.8267 | 2.5927 | 2.3547 | 2.1137 | 0.84671 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROSSHILLS | 11 | 33 | Silsden | BRADFORD WEST | BD20 7AQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROWLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN17 4BB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROWN STREET | 11 | 33 | Girlington | BRADFORD WEST | BD1 2LA | ST (DFES) | 0.78271 | 0.77471 | 0.76571 | 0.75571 | 0.74271 | 0.72271 | 0.70171 | 0.67571 | 0.64971 | 0.62371 | 0.48571 | 0.34971 | 0.22771 | 0.12871 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DALTON | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD2 1FF | ST (DFES) | 2.705 | 2.631 | 2.54 | 2.432 | 2.309 | 2.1 | 1.887 | 1.632 | 1.372 | 1.107 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DARNALL | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 4JT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DEARNE ROAD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DEIGHTON | 11 | 33 | Brighouse 132/33kV | ELLAND | HD2 1UP | ST (DFES) | 18.45 | 18.408 | 18.356 | 18.294 | 18.223 | 18.104 | 17.982 | 17.836 | 17.688 | 17.536 | 16.739 | 15.96 | 15.253 | 14.682 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENBY DALE ROAD | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7BH | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENBY GRANGE | 11 | 33 | Thornhill 132kV | ELLAND | WF4 4JG | ST (DFES) | 0.32211 | 0.30711 | 0.28911 | 0.26711 | 0.24211 | 0.20111 | 0.15911 | 0.10811 | 0.05711 | 0.0031098 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENHOLME | 11 | 33 | Holmfield | BRADFORD WEST | BD13 4JF | ST (DFES) | 11.6027 | 11.5877 | 11.5687 | 11.5467 | 11.5217 | 11.4777 | 11.4347 | 11.3817 | 11.3277 | 11.2737 | 10.9877 | 10.7067 | 10.4527 | 10.2477 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DINNINGTON | 11 | 66 | Thurcroft | THURCROFT | S25 3QT | ST (DFES) | 0 | 22.4157 | 22.3407 | 22.2517 | 22.1507 | 21.9837 | 21.8137 | 21.6097 | 21.4007 | 21.1827 | 20.0257 | 18.9467 | 17.9487 | 17.1317 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DOUGHTY ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN32 0LR | ST (DFES) | 3.8908 | 3.8058 | 3.6988 | 3.5728 | 3.4288 | 3.1918 | 2.9498 | 2.6588 | 2.3618 | 2.0528 | 0.4148 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DOWKER STREET | 11 | 33 | Lindley | ELLAND | HD3 4JB | ST (DFES) | 0.51751 | 0.47851 | 0.43051 | 0.37351 | 0.30951 | 0.19951 | 0.087515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRAX PRIMARY | 11 | 66 | Camblesforth | CAMBLESFORTH | YO8 6PQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 5XR | ST (DFES) | 13.8945 | 13.7685 | 13.6085 | 13.4195 | 13.2165 | 12.8955 | 12.5635 | 12.1685 | 11.7585 | 11.3235 | 8.9635 | 6.8925 | 4.9315 | 3.3035 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRONFIELD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S18 2XU | ST (DFES) | 1.6972 | 1.6662 | 1.6292 | 1.5852 | 1.5352 | 1.4522 | 1.3672 | 1.2652 | 1.1612 | 1.0552 | 0.4902 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DUDLEY HILL | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9NW | ST (DFES) | 23.1648 | 23.1348 | 23.0978 | 23.0538 | 23.0038 | 22.9178 | 22.8308 | 22.7268 | 22.6198 | 22.5118 | 21.9448 | 21.3858 | 20.8808 | 20.4728 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DUNKESWICK | 11 | 33 | Bramham | FERRYBRIDGE B | LS17 9LP | ST (DFES) | 12.0553 | 12.0163 | 11.9603 | 11.8933 | 11.8233 | 11.7303 | 11.6303 | 11.5123 | 11.3843 | 11.2343 | 10.3633 | 9.7843 | 9.1593 | 8.5983 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DURKAR LOW LANE | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF4 3BJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EASINGTON | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0SU | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EASTFIELD ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ECCLESFIELD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 9YR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EDLINGTON | 11 | 66 | Thurcroft | THURCROFT | DN12 1SU | ST (DFES) | 13.5995 | 13.5275 | 13.4385 | 13.3315 | 13.2125 | 13.0155 | 12.8135 | 12.5725 | 12.3255 | 12.0685 | 10.7015 | 9.4245 | 8.2445 | 7.2795 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EGGBOROUGH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | DN14 0QA | ST (DFES) | 7.4356 | 7.4206 | 7.4026 | 7.3816 | 7.3586 | 7.3226 | 7.2846 | 7.2406 | 7.1946 | 7.1446 | 6.8756 | 6.6436 | 6.4226 | 6.2376 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELGAR ROAD | 11 | 33 | Hull West | CREYKE BECK | HU4 7NY | ST (DFES) | 21.9997 | 21.8967 | 21.7667 | 21.6137 | 21.4457 | 21.1747 | 20.8957 | 20.5627 | 20.2187 | 19.8587 | 17.9227 | 16.1687 | 14.5287 | 13.1787 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLAND 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX5 9AE | ST (DFES) | 19.9975 | 19.9605 | 19.9155 | 19.8625 | 19.8015 | 19.6985 | 19.5945 | 19.4685 | 19.3415 | 19.2115 | 18.5325 | 17.8605 | 17.2545 | 16.7665 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIFOOT LANE | 11 | 33 | Saltend 132/33kV | SALTEND NORTH | HU12 9EB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 1/3 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | ST (DFES) | 4.8108 | 4.7838 | 4.7508 | 4.7118 | 4.6668 | 4.5898 | 4.5128 | 4.4188 | 4.3248 | 4.2278 | 3.7228 | 3.2238 | 2.7738 | 2.4098 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 2 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 1 | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 4LS | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 2 | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S75 4LS | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELSECAR | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S74 8AU | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ENDIKE LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 8AY | ST (DFES) | 16.5394 | 16.4774 | 16.4004 | 16.3104 | 16.2084 | 16.0404 | 15.8674 | 15.6614 | 15.4504 | 15.2324 | 14.0714 | 12.9784 | 11.9714 | 11.1504 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EPWORTH | 11 | 33 | Blyton | KEADBY | DN9 1JU | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FARNLEY CRESCENT | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 5AN | ST (DFES) | 0.85608 | 0.80308 | 0.73908 | 0.66208 | 0.57408 | 0.42608 | 0.27508 | 0.093077 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FENTON LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6EZ | ST (DFES) | 5.1032 | 5.0822 | 5.0542 | 5.0212 | 4.9862 | 4.9322 | 4.8752 | 4.8082 | 4.7382 | 4.6632 | 4.2552 | 3.9032 | 3.5672 | 3.2872 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF11 8RR | ST (DFES) | 2.194 | 2.09 | 1.96 | 1.806 | 1.634 | 1.355 | 1.068 | 0.726 | 0.373 | 0.003 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIR TREE LANE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS17 7BZ | ST (DFES) | 3.8828 | 3.8168 | 3.7348 | 3.6388 | 3.5278 | 3.3408 | 3.1508 | 2.9218 | 2.6898 | 2.4518 | 1.1998 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIRST AVENUE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 9NE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIRTH BROWN | 11 | 33 | Santon | KEADBY | DN16 1XP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FISH DAM LANE | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 3HQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FLIXBOROUGH | 11 | 33 | Scunthorpe North | KEADBY | DN15 8RR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOLLY HALL | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 3TF | ST (DFES) | 1.8147 | 1.7827 | 1.7437 | 1.6977 | 1.6457 | 1.5567 | 1.4657 | 1.3567 | 1.2457 | 1.1327 | 0.5387 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOUR LANE ENDS | 11 | 33 | Girlington | BRADFORD WEST | BD8 0LJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOXHILLS | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FULLERTON ROAD | 11 | 33 | Templeborough 275/33KV | TEMPLEBOROUGH 275/33KV | S60 1DL | ST (DFES) | 0.11587 | 0.09187 | 0.06187 | 0.02587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FURNESS AVENUE | 11 | 33 | Holmfield | BRADFORD WEST | WF8 3JA | ST (DFES) | 1.1489 | 1.0909 | 1.0209 | 0.93886 | 0.84486 | 0.68486 | 0.52186 | 0.32686 | 0.12786 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GAISBY LANE | 11 | 33 | Bradford | BRADFORD WEST | BD2 1BB | ST (DFES) | 3.141 | 3.087 | 3.02 | 2.942 | 2.851 | 2.697 | 2.54 | 2.353 | 2.161 | 1.967 | 0.94698 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIBRALTAR ROAD | 11 | 33 | Holmfield | BRADFORD WEST | HX1 4HL | ST (DFES) | 4.3461 | 4.2661 | 4.1701 | 4.0561 | 3.9261 | 3.7051 | 3.4811 | 3.2121 | 2.9391 | 2.6601 | 1.2061 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIBSON LANE | 11 | 33 | Hull West | CREYKE BECK | HU14 3HH | ST (DFES) | 17.101 | 17.005 | 16.885 | 16.743 | 16.589 | 16.348 | 16.098 | 15.8 | 15.491 | 15.163 | 13.386 | 11.826 | 10.348 | 9.122 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GILDERSOME | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 7HW | ST (DFES) | 0.66387 | 0.63387 | 0.59687 | 0.55387 | 0.50387 | 0.41887 | 0.33287 | 0.22987 | 0.12387 | 0.016867 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GLEADLESS VALLEY | 11 | 33 | Norton Lees | NORTON LEES | S14 1FP | ST (DFES) | 1.785 | 1.729 | 1.661 | 1.58 | 1.486 | 1.327 | 1.166 | 0.97198 | 0.77498 | 0.57398 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GOOLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 6SX | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GRAINTHORPE | 11 | 33 | Wold Newton | KEADBY | LN11 7JU | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREAT COATES | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN37 9PN | ST (DFES) | 2.1871 | 2.1201 | 2.0361 | 1.9361 | 1.8231 | 1.6391 | 1.4501 | 1.2241 | 0.99209 | 0.75009 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREENHILL | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 7RJ | ST (DFES) | 0.87723 | 0.84323 | 0.80223 | 0.75423 | 0.69823 | 0.60423 | 0.50823 | 0.39323 | 0.27623 | 0.15623 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS RD | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GRIMETHORPE | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S72 7BQ | ST (DFES) | 15.5559 | 15.5239 | 15.4849 | 15.4389 | 15.3869 | 15.3009 | 15.2129 | 15.1069 | 14.9989 | 14.8869 | 14.2889 | 13.7309 | 13.2149 | 12.7929 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GROVE STREET | 11 | 33 | Lindley | ELLAND | HD1 2PB | ST (DFES) | 13.6802 | 13.6692 | 13.6562 | 13.6412 | 13.6232 | 13.5922 | 13.5622 | 13.5252 | 13.4872 | 13.4492 | 13.2472 | 13.0502 | 12.8712 | 12.7262 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GUARDIAN GLASS | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8GA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HACKENTHORPE | 11 | 66 | Thurcroft | THURCROFT | S12 4ET | ST (DFES) | 24.2326 | 24.1756 | 24.1066 | 24.0236 | 23.9296 | 23.7686 | 23.6046 | 23.4076 | 23.2076 | 23.0046 | 21.9406 | 20.8886 | 19.9386 | 19.1736 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 33/11KV | 11 | 33 | Halifax 132/33kV | ELLAND | HX1 1XB | ST (DFES) | 2.4206 | 2.3686 | 2.3046 | 2.2306 | 2.1446 | 1.9996 | 1.8526 | 1.6756 | 1.4956 | 1.3126 | 0.35662 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALLAM STREET | 11 | 33 | Menston | BRADFORD WEST | LS20 8AG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARDEN | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 1BG | ST (DFES) | 6.1403 | 6.1243 | 6.1043 | 6.0803 | 6.0533 | 6.0073 | 5.9603 | 5.9043 | 5.8473 | 5.7883 | 5.4833 | 5.1823 | 4.9103 | 4.6913 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARPSWELL | 11 | 33 | Blyton | KEADBY | DN21 5UT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARWORTH | 11 | 66 | Thurcroft | THURCROFT | DN11 8JW | ST (DFES) | 19.5805 | 19.5505 | 19.5115 | 19.4645 | 19.4135 | 19.3355 | 19.2545 | 19.1575 | 19.0555 | 18.9465 | 18.3495 | 17.8455 | 17.3595 | 16.9505 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 1 | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD22 9EP | ST (DFES) | 13.6766 | 13.6516 | 13.6216 | 13.5856 | 13.5436 | 13.4736 | 13.4016 | 13.3156 | 13.2286 | 13.1396 | 12.6736 | 12.2136 | 11.7986 | 11.4636 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 2 | 11 | 33 | Silsden | BRADFORD WEST | BD22 9EP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAXEY | 11 | 33 | Blyton | KEADBY | DN9 2LT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAYTON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1RJ | ST (DFES) | 0 | 0 | 0 | 16.2495 | 16.1375 | 15.9625 | 15.7805 | 15.5645 | 15.3395 | 15.1015 | 13.8095 | 12.6755 | 11.6015 | 10.7095 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAZLEHEAD | 11 | 33 | Thornhill 132kV | ELLAND | S36 4HG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEBDEN BRIDGE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 6LX | ST (DFES) | 7.4947 | 7.4787 | 7.4597 | 7.4367 | 7.4107 | 7.3657 | 7.3207 | 7.2667 | 7.2117 | 7.1557 | 6.8637 | 6.5737 | 6.3117 | 6.1017 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEDLEY CHASE | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 1YN | ST (DFES) | 12.6968 | 12.6838 | 12.6688 | 12.6498 | 12.6288 | 12.5938 | 12.5568 | 12.5138 | 12.4688 | 12.4238 | 12.1848 | 11.9518 | 11.7408 | 11.5698 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEDON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 8ED | ST (DFES) | 11.4115 | 11.4075 | 11.4025 | 11.3965 | 11.3905 | 11.3795 | 11.3675 | 11.3545 | 11.3405 | 11.3255 | 11.2515 | 11.1785 | 11.1125 | 11.0595 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEMSWORTH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 5BZ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 1 | 11 | 33 | Hull South | CREYKE BECK | HU4 6SP | ST (DFES) | 0.87284 | 0.84784 | 0.81684 | 0.77984 | 0.73984 | 0.67484 | 0.60884 | 0.52884 | 0.44684 | 0.36084 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 2 | 11 | 33 | Hull West | CREYKE BECK | HU4 6SP | ST (DFES) | 1.4975 | 1.4735 | 1.4445 | 1.4095 | 1.3715 | 1.3095 | 1.2455 | 1.1695 | 1.0905 | 1.0085 | 0.56952 | 0.16652 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HIBALDSTOW | 11 | 33 | Santon | KEADBY | DN21 4NH | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HICKLETON | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 0DE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HILLCREST | 11 | 33 | Leeds East | SKELTON GRANGE | LS8 3AA | ST (DFES) | 3.5199 | 3.4569 | 3.3789 | 3.2859 | 3.1799 | 3.0009 | 2.8189 | 2.6009 | 2.3779 | 2.1499 | 0.95293 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLBECK | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9SZ | ST (DFES) | 4.063 | 4.014 | 3.955 | 3.884 | 3.803 | 3.666 | 3.526 | 3.359 | 3.189 | 3.015 | 2.099 | 1.207 | 0.39602 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLDERNESS | 11 | 33 | Bransholme | CREYKE BECK | HU9 4AU | ST (DFES) | 0.14951 | 0.062508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 4BX | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 20.5555 | 20.4815 | 20.3935 | 20.3015 | 20.2045 | 19.6765 | 19.2155 | 18.7785 | 18.4145 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HONLEY | 11 | 33 | Lindley | ELLAND | HD9 6RU | ST (DFES) | 10.4289 | 10.3769 | 10.3129 | 10.2379 | 10.1519 | 10.0059 | 9.8579 | 9.6799 | 9.4979 | 9.3129 | 8.3419 | 7.3909 | 6.5289 | 5.8329 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOPE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S33 6RP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HORBURY | 11 | 33 | Thornhill 132kV | ELLAND | WF4 6EU | ST (DFES) | 17.9753 | 17.9203 | 17.8513 | 17.7703 | 17.6773 | 17.5263 | 17.3703 | 17.1853 | 16.9943 | 16.7953 | 15.7353 | 14.7533 | 13.8423 | 13.0953 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOUGHTON MAIN | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S72 0GX | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 33/11KV | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5NP | ST (DFES) | 22.7486 | 22.6716 | 22.5746 | 22.4606 | 22.3366 | 22.1396 | 21.9356 | 21.6926 | 21.4406 | 21.1756 | 19.7416 | 18.4656 | 17.2636 | 16.2696 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUMBER ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LZ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNMANBY | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO14 0JY | ST (DFES) | 20.2485 | 20.1895 | 20.1065 | 20.0075 | 19.9055 | 19.7675 | 19.6195 | 19.4455 | 19.2555 | 19.0365 | 17.7735 | 16.9095 | 15.9905 | 15.1735 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ICI FIBRES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4LT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IDLE | 11 | 33 | Bradford | BRADFORD WEST | BD10 8SA | ST (DFES) | 2.6581 | 2.5991 | 2.5271 | 2.4411 | 2.3431 | 2.1761 | 2.0061 | 1.8031 | 1.5961 | 1.3851 | 0.28005 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ILKLEY | 11 | 33 | Silsden | BRADFORD WEST | LS29 9BE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | INGS LANE | 11 | 33 | Silsden | BRADFORD WEST | BD23 1UP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IVESON HOUSE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 6RF | ST (DFES) | 20.8906 | 20.8306 | 20.7576 | 20.6696 | 20.5696 | 20.4016 | 20.2296 | 20.0236 | 19.8136 | 19.5996 | 18.4706 | 17.3716 | 16.3726 | 15.5646 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | JARRATT STREET | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN1 2BS | ST (DFES) | 13.1098 | 13.0708 | 13.0228 | 12.9658 | 12.9018 | 12.7968 | 12.6888 | 12.5598 | 12.4268 | 12.2888 | 11.5568 | 10.8728 | 10.2408 | 9.7238 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KEDDINGTON ROAD | 11 | 33 | Wold Newton | KEADBY | LN11 0DE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KEIGHLEY | 11 | 132 | Keighley | BRADFORD WEST | BD21 5AJ | ST (DFES) | 30.4249 | 30.3919 | 30.3519 | 30.3039 | 30.2489 | 30.1549 | 30.0599 | 29.9449 | 29.8289 | 29.7099 | 29.0899 | 28.4779 | 27.9249 | 27.4789 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KENMORE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 0XE | ST (DFES) | 18.8869 | 18.8619 | 18.8309 | 18.7939 | 18.7519 | 18.6829 | 18.6119 | 18.5279 | 18.4409 | 18.3499 | 17.8679 | 17.4219 | 17.0069 | 16.6669 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KILLINGHALL ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD3 8HN | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KILNHURST | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S64 5TL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KING GEORGE DOCK | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5PL | ST (DFES) | 23.859 | 23.856 | 23.853 | 23.848 | 23.843 | 23.835 | 23.826 | 23.816 | 23.805 | 23.794 | 23.738 | 23.682 | 23.632 | 23.591 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRK DRIVE | 11 | 33 | Menston | BRADFORD WEST | BD17 6SA | ST (DFES) | 1.0644 | 1.0234 | 0.97438 | 0.91538 | 0.84838 | 0.73338 | 0.61738 | 0.47738 | 0.33538 | 0.19038 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRK SANDALL | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 1QP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKBURN | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 9EH | ST (DFES) | 6.1592 | 6.1312 | 6.0952 | 6.0522 | 6.0072 | 5.9372 | 5.8652 | 5.7792 | 5.6892 | 5.5922 | 5.0552 | 4.6102 | 4.1792 | 3.8142 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIVETON PARK | 11 | 66 | Thurcroft | THURCROFT | S26 6RP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KNOSTROP | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0PJ | ST (DFES) | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEA ROAD | 11 | 33 | Blyton | KEADBY | DN21 1ND | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEASOWE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 2EY | ST (DFES) | 6.849 | 6.817 | 6.778 | 6.731 | 6.678 | 6.588 | 6.496 | 6.386 | 6.274 | 6.159 | 5.556 | 4.969 | 4.435 | 4.003 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEDSTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF10 2AX | ST (DFES) | 1.3198 | 1.2728 | 1.2148 | 1.1458 | 1.0668 | 0.9338 | 0.7978 | 0.6358 | 0.4698 | 0.3008 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS ROAD | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 5AA | ST (DFES) | 0.39249 | 0.37149 | 0.34649 | 0.31649 | 0.28249 | 0.22549 | 0.16749 | 0.097491 | 0.025491 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEGRAMS MILL LANE | 11 | 33 | Girlington | BRADFORD WEST | BD7 2BA | ST (DFES) | 21.2458 | 21.2118 | 21.1708 | 21.1208 | 21.0648 | 20.9688 | 20.8708 | 20.7538 | 20.6348 | 20.5138 | 19.8778 | 19.2518 | 18.6848 | 18.2288 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEYLANDS ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS2 7QB | ST (DFES) | 16.1512 | 16.1422 | 16.1302 | 16.1172 | 16.1012 | 16.0752 | 16.0482 | 16.0162 | 15.9832 | 15.9492 | 15.7732 | 15.6012 | 15.4442 | 15.3182 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LIVERSEDGE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF15 7NY | ST (DFES) | 1.7829 | 1.7469 | 1.7019 | 1.6489 | 1.5889 | 1.4869 | 1.3839 | 1.2589 | 1.1319 | 1.0029 | 0.32288 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOUTH | 11 | 33 | Wold Newton | KEADBY | LN11 0WA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOW MOOR | 11 | 33 | Staygate | SKELTON GRANGE | BD12 0NG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOWFIELDS | 11 | 33 | Brighouse 132/33kV | ELLAND | HX5 9DE | ST (DFES) | 25.258 | 25.256 | 25.255 | 25.253 | 25.251 | 25.248 | 25.244 | 25.24 | 25.235 | 25.231 | 25.208 | 25.185 | 25.164 | 25.148 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOXLEY ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 6SJ | ST (DFES) | 0.24826 | 0.24526 | 0.24126 | 0.23726 | 0.23126 | 0.22226 | 0.21226 | 0.20126 | 0.19026 | 0.17826 | 0.11726 | 0.056257 | 0.0022569 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANCHESTER ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD5 0QL | ST (DFES) | 3.0867 | 3.0757 | 3.0637 | 3.0487 | 3.0317 | 3.0027 | 2.9737 | 2.9377 | 2.9017 | 2.8657 | 2.6737 | 2.4847 | 2.3137 | 2.1757 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 1 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S12 2DL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 2 | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S12 2DL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARKHAM GATES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 2FS | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARMION ROAD | 11 | 33 | Norton Lees | NORTON LEES | S11 8TS | ST (DFES) | 2.6488 | 2.5748 | 2.4848 | 2.3788 | 2.2568 | 2.0478 | 1.8358 | 1.5818 | 1.3238 | 1.0608 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARSDEN ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN31 3SQ | ST (DFES) | 5.0239 | 4.9899 | 4.9489 | 4.8989 | 4.8429 | 4.7509 | 4.6559 | 4.5419 | 4.4259 | 4.3059 | 3.6659 | 3.0649 | 2.5099 | 2.0569 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARTONGATE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 6RX | ST (DFES) | 0 | 0 | 0 | 19.2205 | 19.0255 | 18.7175 | 18.3995 | 18.0205 | 17.6265 | 17.2095 | 14.9465 | 12.9605 | 11.0785 | 9.5175 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MELTHAM | 11 | 33 | Lindley | ELLAND | HD9 4AL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MEXBOROUGH 1_2 | 11 | 66 | Thurcroft | THURCROFT | S64 0JD | ST (DFES) | 24.662 | 24.561 | 24.436 | 24.287 | 24.119 | 23.844 | 23.562 | 23.225 | 22.878 | 22.519 | 20.606 | 18.819 | 17.168 | 15.818 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MIDDLETON TOWN STREET | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS10 3TQ | ST (DFES) | 16.401 | 16.348 | 16.283 | 16.206 | 16.118 | 15.97 | 15.818 | 15.637 | 15.451 | 15.262 | 14.267 | 13.298 | 12.418 | 11.705 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILLHOUSES | 11 | 33 | Jordanthorpe | JORDANTHORPE | S7 2QH | ST (DFES) | 1.2795 | 1.2535 | 1.2205 | 1.1815 | 1.1365 | 1.0605 | 0.98352 | 0.89052 | 0.79652 | 0.70052 | 0.19852 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILLROYD STREET | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1JZ | ST (DFES) | 14.3257 | 14.2727 | 14.2087 | 14.1337 | 14.0477 | 13.9017 | 13.7537 | 13.5757 | 13.3937 | 13.2097 | 12.2467 | 11.2927 | 10.4327 | 9.7397 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILTON PLACE | 11 | 33 | Wakefield North | SKELTON GRANGE | WF5 9EG | ST (DFES) | 18.6927 | 18.6247 | 18.5407 | 18.4407 | 18.3277 | 18.1407 | 17.9497 | 17.7207 | 17.4857 | 17.2427 | 15.9457 | 14.7347 | 13.6157 | 12.6997 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MIRFIELD | 11 | 33 | Thornhill 132kV | ELLAND | WF14 8NF | ST (DFES) | 19.583 | 19.518 | 19.439 | 19.344 | 19.236 | 19.053 | 18.867 | 18.644 | 18.417 | 18.184 | 16.965 | 15.773 | 14.692 | 13.819 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MONCKTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S71 4BG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOOR ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS6 4BJ | ST (DFES) | 23.2626 | 23.1936 | 23.1096 | 23.0096 | 22.8956 | 22.7016 | 22.5046 | 22.2686 | 22.0276 | 21.7816 | 20.4866 | 19.2266 | 18.0806 | 17.1536 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOORSIDE ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD2 3RJ | ST (DFES) | 20.2239 | 20.1619 | 20.0869 | 19.9969 | 19.8939 | 19.7189 | 19.5409 | 19.3269 | 19.1099 | 18.8889 | 17.7289 | 16.5869 | 15.5539 | 14.7209 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MORLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 9HS | ST (DFES) | 19.8647 | 19.8127 | 19.7497 | 19.6737 | 19.5877 | 19.4407 | 19.2927 | 19.1137 | 18.9317 | 18.7467 | 17.7687 | 16.8167 | 15.9517 | 15.2517 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOUNT STREET | 11 | 33 | Bradford | BRADFORD WEST | BD4 8TB | ST (DFES) | 21.018 | 21.003 | 20.985 | 20.964 | 20.939 | 20.897 | 20.855 | 20.804 | 20.752 | 20.7 | 20.423 | 20.151 | 19.905 | 19.707 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MYTHOLMROYD | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 8NE | ST (DFES) | 13.7861 | 13.7571 | 13.7211 | 13.6801 | 13.6321 | 13.5511 | 13.4691 | 13.3701 | 13.2701 | 13.1681 | 12.6351 | 12.1071 | 11.6311 | 11.2481 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NAB LANE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 9NE | ST (DFES) | 12.0116 | 11.9786 | 11.9386 | 11.8916 | 11.8376 | 11.7456 | 11.6526 | 11.5406 | 11.4276 | 11.3106 | 10.7006 | 10.1046 | 9.5626 | 9.1256 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NABWOOD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD18 4AA | ST (DFES) | 13.4451 | 13.3971 | 13.3381 | 13.2691 | 13.1901 | 13.0551 | 12.9171 | 12.7521 | 12.5851 | 12.4141 | 11.5191 | 10.6381 | 9.8411 | 9.1981 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NATIONAL AVENUE | 11 | 33 | Hull South | CREYKE BECK | HU5 4JN | ST (DFES) | 0.79437 | 0.76637 | 0.73137 | 0.69037 | 0.64337 | 0.56237 | 0.48037 | 0.38137 | 0.28137 | 0.17937 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | Wincobank | WINCOBANK | S61 2DL | ST (DFES) | 18.9692 | 18.9222 | 18.8632 | 18.7942 | 18.7152 | 18.5852 | 18.4522 | 18.2932 | 18.1302 | 17.9602 | 17.0582 | 16.2162 | 15.4382 | 14.8012 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEW ORCHARD LANE | 11 | 66 | Thurcroft | THURCROFT | S66 9HY | ST (DFES) | 1.2352 | 1.1952 | 1.1442 | 1.0832 | 1.0152 | 0.90315 | 0.78815 | 0.65015 | 0.50915 | 0.36215 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWHALL ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 2RS | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4083 | 1.3583 | 1.3073 | 1.0403 | 0.7763 | 0.5383 | 0.3463 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 1 | 11 | 33 | Hull West | CREYKE BECK | HU15 2QU | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 2 | 11 | 33 | Osgodby 3/4 | DRAX | HU15 2QU | ST (DFES) | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NINELANDS LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS25 2PE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORFOLK PARK | 11 | 33 | Norton Lees | NORTON LEES | S2 3UU | ST (DFES) | 0.63039 | 0.57539 | 0.50839 | 0.42939 | 0.33739 | 0.18239 | 0.024393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORMANBY | 11 | 33 | Blyton | KEADBY | LN8 2HQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORMANTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF6 2JA | ST (DFES) | 4.6317 | 4.5797 | 4.5147 | 4.4377 | 4.3507 | 4.2077 | 4.0607 | 3.8857 | 3.7047 | 3.5177 | 2.5157 | 1.5887 | 0.7287 | 0.023698 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORTH AVENUE | 11 | 33 | Menston | BRADFORD WEST | LS21 1SX | ST (DFES) | 19.2336 | 19.1876 | 19.1306 | 19.0626 | 18.9856 | 18.8546 | 18.7216 | 18.5616 | 18.3986 | 18.2326 | 17.3576 | 16.5046 | 15.7306 | 15.1036 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORTH THORESBY | 11 | 33 | Wold Newton | KEADBY | DN36 5SB | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORWOOD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 9JR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OAKES ROAD | 11 | 33 | Lindley | ELLAND | HD3 3EW | ST (DFES) | 2.5558 | 2.4988 | 2.4298 | 2.3478 | 2.2528 | 2.0938 | 1.9308 | 1.7358 | 1.5378 | 1.3348 | 0.27082 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OAKWOOD LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 3LF | ST (DFES) | 19.5911 | 19.5491 | 19.4981 | 19.4381 | 19.3691 | 19.2521 | 19.1321 | 18.9901 | 18.8441 | 18.6951 | 17.9121 | 17.1491 | 16.4561 | 15.8961 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ODSAL | 11 | 33 | Staygate | SKELTON GRANGE | BD6 1BW | ST (DFES) | 2.7086 | 2.6566 | 2.5926 | 2.5176 | 2.4306 | 2.2836 | 2.1336 | 1.9536 | 1.7716 | 1.5846 | 0.6096 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OLYMPIA MILLS | 11 | 33 | Osgodby 3/4 | DRAX | YO8 7AG | ST (DFES) | 19.8251 | 19.7441 | 19.6411 | 19.5191 | 19.3881 | 19.1841 | 18.9721 | 18.7201 | 18.4571 | 18.1771 | 16.6501 | 15.3351 | 14.0791 | 13.0311 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ORGREAVE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 9NA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OUTWOOD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF3 3TA | ST (DFES) | 1.8477 | 1.7937 | 1.7267 | 1.6467 | 1.5557 | 1.4057 | 1.2517 | 1.0677 | 0.87966 | 0.68466 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK HILL | 11 | 33 | Sheffield City | SHEFFIELD CITY | S2 5QY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4182 | 1.3412 | 1.2622 | 0.84723 | 0.43923 | 0.069226 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK ROAD | 11 | 33 | Thornhill 132kV | ELLAND | WF12 9LW | ST (DFES) | 1.2018 | 1.1548 | 1.0978 | 1.0308 | 0.95283 | 0.82183 | 0.68883 | 0.52883 | 0.36583 | 0.19883 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK STREET | 11 | 132 | Park Street | WEST MELTON / THORPE MARSH | S61 1TF | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PASTURE ROAD SOUTH | 11 | 33 | Santon | KEADBY | DN18 5RX | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PATRINGTON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0AD | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 6BG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 2FL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PLANGEO | 11 | 33 | Hull South | CREYKE BECK | HU3 6EG | ST (DFES) | 3.6054 | 3.5474 | 3.4774 | 3.3934 | 3.2964 | 3.1314 | 2.9634 | 2.7624 | 2.5574 | 2.3494 | 1.2604 | 0.18337 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | POLLINGTON | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | DN14 0RR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0JG | ST (DFES) | 1.7478 | 1.7338 | 1.7168 | 1.6968 | 1.6738 | 1.6358 | 1.5958 | 1.5488 | 1.4998 | 1.4508 | 1.1918 | 0.93876 | 0.70976 | 0.52376 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | POOL | 11 | 33 | Menston | BRADFORD WEST | LS21 1RP | ST (DFES) | 16.3975 | 16.3875 | 16.3735 | 16.3575 | 16.3385 | 16.3095 | 16.2795 | 16.2445 | 16.2075 | 16.1685 | 15.9565 | 15.7695 | 15.5935 | 15.4465 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PRINCE OF WALES | 11 | 33 | Featherstone | FERRYBRIDGE B | WF8 4PR | ST (DFES) | 10.9075 | 10.8475 | 10.7735 | 10.6855 | 10.5855 | 10.4215 | 10.2535 | 10.0535 | 9.8465 | 9.6325 | 8.4865 | 7.4265 | 6.4425 | 5.6345 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PROSPECT ROAD | 11 | 33 | Lindley | ELLAND | HD3 4UY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | QUEENS ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 2LZ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | QUEENSBURY | 11 | 33 | Holmfield | BRADFORD WEST | HX3 7TJ | ST (DFES) | 25.5614 | 25.4904 | 25.4044 | 25.3034 | 25.1874 | 24.9904 | 24.7894 | 24.5494 | 24.3044 | 24.0554 | 22.7524 | 21.4654 | 20.3024 | 19.3654 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWCLIFFE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8PQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWDON | 11 | 33 | Rodley | SKELTON GRANGE | LS19 7BZ | ST (DFES) | 23.8976 | 23.8506 | 23.7936 | 23.7256 | 23.6476 | 23.5156 | 23.3816 | 23.2216 | 23.0576 | 22.8896 | 22.0096 | 21.1526 | 20.3736 | 19.7426 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | Rawmarsh Road 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | Rawmarsh Road 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON ROAD | 11 | 33 | Girlington | BRADFORD WEST | BD1 3SH | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON SPRING ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 1PD | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3368 | 3.2518 | 3.1638 | 2.7078 | 2.2568 | 1.8498 | 1.5208 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | REVILL LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 7QX | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROCKWARE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4RH | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY LANE | 11 | 33 | Rodley | SKELTON GRANGE | LS13 1LJ | ST (DFES) | 0.79021 | 0.73721 | 0.67221 | 0.59621 | 0.50821 | 0.35921 | 0.20821 | 0.027205 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROMAN AVENUE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 2DY | ST (DFES) | 20.5256 | 20.4816 | 20.4276 | 20.3636 | 20.2906 | 20.1666 | 20.0406 | 19.8896 | 19.7356 | 19.5786 | 18.7506 | 17.9446 | 17.2116 | 16.6196 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROYDS LANE | 11 | 33 | Wakefield North | SKELTON GRANGE | LS26 0BE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | ST (DFES) | 11.9208 | 11.9038 | 11.8818 | 11.8568 | 11.8278 | 11.7798 | 11.7298 | 11.6698 | 11.6098 | 11.5478 | 11.2228 | 10.9058 | 10.6168 | 10.3848 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT STREET | 11 | 33 | Girlington | BRADFORD WEST | BD7 4EH | ST (DFES) | 12.4446 | 12.4136 | 12.3766 | 12.3326 | 12.2816 | 12.1946 | 12.1066 | 12.0006 | 11.8926 | 11.7836 | 11.2096 | 10.6436 | 10.1326 | 9.7196 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTERFORTH | 11 | 33 | Silsden | BRADFORD WEST | BB18 6JD | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTERHEBBLE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX3 0QH | ST (DFES) | 19.5816 | 19.5276 | 19.4626 | 19.3856 | 19.2976 | 19.1486 | 18.9976 | 18.8156 | 18.6306 | 18.4426 | 17.4606 | 16.4866 | 15.6086 | 14.9026 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTSHOUSE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU8 9HR | ST (DFES) | 21.3762 | 21.3392 | 21.2932 | 21.2392 | 21.1762 | 21.0692 | 20.9612 | 20.8302 | 20.6972 | 20.5622 | 19.8572 | 19.1582 | 18.5282 | 18.0192 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SANDHILL LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO41 4DF | ST (DFES) | 0.3227 | 0.3047 | 0.2817 | 0.2547 | 0.2257 | 0.1797 | 0.1317 | 0.074702 | 0.016702 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAXON ROAD | 11 | 33 | Norton Lees | NORTON LEES | S8 0XQ | ST (DFES) | 2.2842 | 2.2312 | 2.1672 | 2.0912 | 2.0032 | 1.8542 | 1.7032 | 1.5212 | 1.3362 | 1.1482 | 0.16418 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCARTHO | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN33 3JL | ST (DFES) | 0.18935 | 0.072354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCHOLES | 11 | 33 | Thornhill 132kV | ELLAND | HD9 1UG | ST (DFES) | 0.92113 | 0.88313 | 0.83613 | 0.78013 | 0.71713 | 0.60913 | 0.50013 | 0.36813 | 0.23513 | 0.098129 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCISSETT | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCULCOATES A | 11 | 132 | Sculcoates A | CREYKE BECK | HU5 1DA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SEACROFT | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 1LU | ST (DFES) | 13.216 | 13.181 | 13.137 | 13.086 | 13.027 | 12.928 | 12.827 | 12.706 | 12.582 | 12.456 | 11.791 | 11.144 | 10.556 | 10.08 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SEATON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU11 5RQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SELBY | 11 | 33 | Osgodby 3/4 | DRAX | YO8 8NB | ST (DFES) | 0.70257 | 0.56657 | 0.39457 | 0.19157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SELBY ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS15 0QE | ST (DFES) | 20.0036 | 19.9446 | 19.8736 | 19.7876 | 19.6906 | 19.5256 | 19.3586 | 19.1576 | 18.9526 | 18.7426 | 17.6406 | 16.5686 | 15.5936 | 14.8046 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHARLSTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF4 1BE | ST (DFES) | 12.0527 | 11.9867 | 11.9047 | 11.8077 | 11.6967 | 11.5157 | 11.3307 | 11.1097 | 10.8817 | 10.6447 | 9.3797 | 8.2087 | 7.1217 | 6.2297 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHEPCOTE TINSLEY | 11 | 33 | Wincobank | WINCOBANK | S9 1RF | ST (DFES) | 30.0977 | 30.0977 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHERBURN | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6PL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHIPLEY | 11 | 33 | Bradford | BRADFORD WEST | DN21 5UT | ST (DFES) | 25.9355 | 25.8975 | 25.8515 | 25.7965 | 25.7335 | 25.6265 | 25.5185 | 25.3875 | 25.2555 | 25.1205 | 24.4125 | 23.7165 | 23.0865 | 22.5775 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHIRLAND LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3GD | ST (DFES) | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILVER STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 2DU | ST (DFES) | 2.7643 | 2.7563 | 2.7453 | 2.7333 | 2.7203 | 2.6963 | 2.6723 | 2.6433 | 2.6143 | 2.5843 | 2.4293 | 2.2753 | 2.1363 | 2.0243 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILVERWOOD | 11 | 66 | Thurcroft | THURCROFT | S65 4PR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SKILLINGS LANE | 11 | 33 | Hull West | CREYKE BECK | HU15 1EQ | ST (DFES) | 2.3894 | 2.3434 | 2.2854 | 2.2174 | 2.1434 | 2.0264 | 1.9064 | 1.7624 | 1.6134 | 1.4554 | 0.59739 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SKIPTON | 11 | 33 | Silsden | BRADFORD WEST | BD23 2RR | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SLAITHWAITE | 11 | 33 | Lindley | ELLAND | HD7 6LS | ST (DFES) | 0.80086 | 0.76186 | 0.71486 | 0.65886 | 0.59486 | 0.48586 | 0.37586 | 0.24286 | 0.10886 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SLEDMERE GARTH | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 5DS | ST (DFES) | 18.749 | 18.726 | 18.697 | 18.663 | 18.623 | 18.557 | 18.49 | 18.409 | 18.327 | 18.243 | 17.801 | 17.37 | 16.979 | 16.663 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SMITH STREET | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 2RY | ST (DFES) | 12.7389 | 12.7029 | 12.6589 | 12.6069 | 12.5469 | 12.4489 | 12.3489 | 12.2289 | 12.1059 | 11.9779 | 11.2989 | 10.6629 | 10.0749 | 9.5949 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SMITHY GREEN | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SNAITHING PARK ROAD | 11 | 33 | Norton Lees | NORTON LEES | S10 3LJ | ST (DFES) | 0.14632 | 0.099323 | 0.042323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SNELSINS LANE | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 3UH | ST (DFES) | 16.3656 | 16.3306 | 16.2866 | 16.2346 | 16.1756 | 16.0756 | 15.9736 | 15.8516 | 15.7266 | 15.5996 | 14.9326 | 14.2786 | 13.6866 | 13.2086 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH ELMSALL | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 2JH | ST (DFES) | 23.1684 | 23.1234 | 23.0674 | 23.0004 | 22.9254 | 22.8014 | 22.6744 | 22.5234 | 22.3674 | 22.2044 | 21.3394 | 20.5374 | 19.7934 | 19.1834 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH FERRIBY | 11 | 33 | Santon | KEADBY | DN18 6JL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH KIRKBY | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 3TJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH RESTON | 11 | 33 | Wold Newton | KEADBY | LN11 8JQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH STREET | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 1AH | ST (DFES) | 7.6789 | 7.6359 | 7.5829 | 7.5199 | 7.4479 | 7.3249 | 7.2009 | 7.0509 | 6.8989 | 6.7449 | 5.9339 | 5.1349 | 4.4119 | 3.8289 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHGATE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 3BE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 19.2426 | 19.1286 | 18.9916 | 18.8486 | 18.6986 | 17.8806 | 17.1636 | 16.4836 | 15.9196 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHWOOD ROAD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU16 5AN | ST (DFES) | 0.12151 | 0.020507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EN | ST (DFES) | 24.2002 | 24.1392 | 24.0642 | 23.9762 | 23.8762 | 23.7062 | 23.5332 | 23.3252 | 23.1142 | 22.8992 | 21.7772 | 20.6652 | 19.6622 | 18.8562 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPARK MILL LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 0TT | ST (DFES) | 5.9092 | 5.8012 | 5.6642 | 5.5032 | 5.3292 | 5.0542 | 4.7712 | 4.4322 | 4.0812 | 3.7092 | 1.6912 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPENBOROUGH | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 5BT | ST (DFES) | 16.5635 | 16.5105 | 16.4455 | 16.3685 | 16.2795 | 16.1305 | 15.9775 | 15.7955 | 15.6095 | 15.4195 | 14.4225 | 13.4475 | 12.5625 | 11.8485 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPRING MILL STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD5 7HF | ST (DFES) | 3.4968 | 3.4728 | 3.4448 | 3.4118 | 3.3728 | 3.3078 | 3.2408 | 3.1608 | 3.0798 | 2.9968 | 2.5628 | 2.1358 | 1.7488 | 1.4368 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAINFORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN7 5HG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAIRFOOT | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 5AD | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STANLEY STREET | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S3 8HG | ST (DFES) | 3.1163 | 3.1003 | 3.0813 | 3.0573 | 3.0313 | 2.9853 | 2.9393 | 2.8843 | 2.8283 | 2.7713 | 2.4713 | 2.1753 | 1.9083 | 1.6923 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STANNINGTON ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 5FH | ST (DFES) | 1.7916 | 1.7136 | 1.6176 | 1.5036 | 1.3736 | 1.1506 | 0.92462 | 0.65362 | 0.37763 | 0.097625 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STATION ROAD | 11 | 33 | Scunthorpe North | KEADBY | DN15 6BT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STEVENSON ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 3XG | ST (DFES) | 1.1752 | 1.1752 | 1.1752 | 1.1752 | 1.1752 | 1.1742 | 1.1742 | 1.1742 | 1.1732 | 1.1732 | 1.1712 | 1.1702 | 1.1682 | 1.1672 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOKE STREET | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3QN | ST (DFES) | 0.146 | 0.145 | 0.145 | 0.144 | 0.144 | 0.143 | 0.141 | 0.14 | 0.139 | 0.137 | 0.13 | 0.123 | 0.116 | 0.111 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 132/11KV | 11 | 132 | Stourton 132/11kV | SKELTON GRANGE | LS10 1SP | ST (DFES) | 1.2741 | 1.2721 | 1.2711 | 1.2691 | 1.2661 | 1.2621 | 1.2591 | 1.2541 | 1.2491 | 1.2441 | 1.2181 | 1.1931 | 1.1701 | 1.1511 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 33/11KV | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1AX | ST (DFES) | 5.608 | 5.586 | 5.56 | 5.528 | 5.492 | 5.43 | 5.368 | 5.293 | 5.217 | 5.138 | 4.728 | 4.328 | 3.965 | 3.671 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOW | 11 | 33 | Blyton | KEADBY | LN1 2AJ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWAN BANK LANE | 11 | 33 | Halifax 132/33kV | ELLAND | HX3 9XT | ST (DFES) | 1.4003 | 1.3633 | 1.3193 | 1.2663 | 1.2063 | 1.1053 | 1.0033 | 0.88035 | 0.75435 | 0.62635 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWEET STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9TZ | ST (DFES) | 7.65 | 7.644 | 7.637 | 7.628 | 7.618 | 7.6 | 7.583 | 7.562 | 7.541 | 7.519 | 7.404 | 7.292 | 7.19 | 7.108 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWINNOW MOOR | 11 | 33 | Rodley | SKELTON GRANGE | LS13 4RJ | ST (DFES) | 2.3675 | 2.3145 | 2.2495 | 2.1715 | 2.0835 | 1.9335 | 1.7805 | 1.5985 | 1.4115 | 1.2205 | 0.21847 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TADCASTER | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9PA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TANKERSLEY PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 2PT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S60 1AD | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNBURY | 11 | 33 | Rodley | SKELTON GRANGE | BD3 7AD | ST (DFES) | 5.0163 | 4.9733 | 4.9223 | 4.8603 | 4.7903 | 4.6713 | 4.5493 | 4.4033 | 4.2553 | 4.1043 | 3.3113 | 2.5323 | 1.8263 | 1.2573 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN8 4NA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNTON | 11 | 33 | Holmfield | BRADFORD WEST | BD13 3DP | ST (DFES) | 19.9732 | 19.9012 | 19.8142 | 19.7112 | 19.5922 | 19.3892 | 19.1842 | 18.9372 | 18.6862 | 18.4312 | 17.0912 | 15.7732 | 14.5802 | 13.6182 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORPE ROAD | 11 | 33 | Osgodby 3/4 | DRAX | DN14 7PA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TICKHILL ROAD | 11 | 66 | Thurcroft | THURCROFT | S66 7QN | ST (DFES) | 29.0804 | 29.0154 | 28.9334 | 28.8364 | 28.7274 | 28.5494 | 28.3664 | 28.1484 | 27.9234 | 27.6894 | 26.4404 | 25.2844 | 24.2114 | 23.3324 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINGLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | WF3 1SS | ST (DFES) | 0.10561 | 0.055615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY PARK ROAD | 11 | 33 | Wincobank | WINCOBANK | S9 5DL | ST (DFES) | 2.8587 | 2.8557 | 2.8517 | 2.8467 | 2.8417 | 2.8327 | 2.8237 | 2.8117 | 2.8007 | 2.7897 | 2.7287 | 2.6687 | 2.6157 | 2.5717 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1TY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TIVERTON ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 4DA | ST (DFES) | 1.4571 | 1.4161 | 1.3651 | 1.3051 | 1.2361 | 1.1181 | 0.99814 | 0.85414 | 0.70814 | 0.55914 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TODMORDEN | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | OL14 7NB | ST (DFES) | 12.813 | 12.772 | 12.722 | 12.664 | 12.597 | 12.483 | 12.368 | 12.229 | 12.088 | 11.945 | 11.196 | 10.454 | 9.785 | 9.247 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TOLLER LANE | 11 | 33 | Girlington | BRADFORD WEST | BD9 5LE | ST (DFES) | 21.2862 | 21.2422 | 21.1892 | 21.1252 | 21.0522 | 20.9292 | 20.8022 | 20.6512 | 20.4972 | 20.3412 | 19.5202 | 18.7122 | 17.9802 | 17.3912 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TONG STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9PP | ST (DFES) | 3.2652 | 3.2422 | 3.2132 | 3.1802 | 3.1412 | 3.0752 | 3.0082 | 2.9282 | 2.8462 | 2.7632 | 2.3262 | 1.8972 | 1.5082 | 1.1952 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | UPPER BASINGHALL STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS1 5JS | ST (DFES) | 4.337 | 4.333 | 4.329 | 4.323 | 4.317 | 4.307 | 4.296 | 4.284 | 4.271 | 4.258 | 4.189 | 4.122 | 4.061 | 4.011 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | VARLEY STREET | 11 | 33 | Rodley | SKELTON GRANGE | LS28 6AN | ST (DFES) | 22.7004 | 22.6534 | 22.5954 | 22.5274 | 22.4484 | 22.3154 | 22.1794 | 22.0174 | 21.8514 | 21.6824 | 20.7914 | 19.9244 | 19.1374 | 18.4994 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | VICTORIA STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4DP | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50742 | 0.46942 | 0.43142 | 0.23142 | 0.033419 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WALESBY | 11 | 33 | Wold Newton | KEADBY | LN8 3UL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WARREN LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9NT | ST (DFES) | 3.8798 | 3.8678 | 3.8518 | 3.8338 | 3.8128 | 3.7778 | 3.7428 | 3.6998 | 3.6568 | 3.6118 | 3.3748 | 3.1488 | 2.9408 | 2.7728 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WATH UPON DEARNE | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DX | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | Wincobank | WINCOBANK | S60 5BL | ST (DFES) | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5026 | 30.5016 | 30.5006 | 30.5006 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAWNE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 5BT | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEELAND ROAD | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 0LA | ST (DFES) | 7.1751 | 7.1531 | 7.1251 | 31.2396 | 31.2016 | 31.1406 | 31.0776 | 31.0016 | 30.9246 | 30.8436 | 30.4136 | 30.0146 | 29.6446 | 29.3416 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WELLINGTON STREET | 11 | 33 | Featherstone | FERRYBRIDGE B | WF10 1NW | ST (DFES) | 12.9411 | 12.9031 | 12.8561 | 12.8001 | 12.7371 | 12.6341 | 12.5281 | 12.4011 | 12.2701 | 12.1351 | 11.4111 | 10.7401 | 10.1181 | 9.6081 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WESLEY CRESCENT | 11 | 33 | Humberston | GRIMSBY WEST | DN35 0JU | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST DOCKS | 11 | 33 | Hull South | CREYKE BECK | HU3 4UU | ST (DFES) | 1.7763 | 1.7743 | 1.7723 | 1.7693 | 1.7663 | 1.7603 | 1.7553 | 1.7483 | 1.7413 | 1.7353 | 1.6993 | 1.6643 | 1.6323 | 1.6063 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST END LANE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN11 0PU | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST MOOR PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3FE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST PARK | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 5PS | ST (DFES) | 7.0876 | 7.0496 | 7.0036 | 6.9486 | 6.8866 | 6.7806 | 6.6726 | 6.5426 | 6.4116 | 6.2766 | 5.5676 | 4.8776 | 4.2496 | 3.7426 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WESTCOTT STREET | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU8 8JN | ST (DFES) | 0.98289 | 0.91489 | 0.83189 | 0.73289 | 0.61889 | 0.42389 | 0.22689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHEATACRE ROAD | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 2GQ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHEATLEY PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4PG | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHINGATE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 3QT | ST (DFES) | 19.8891 | 19.8581 | 19.8191 | 19.7741 | 19.7221 | 19.6351 | 19.5461 | 19.4391 | 19.3301 | 19.2181 | 18.6331 | 18.0631 | 17.5441 | 17.1251 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITE LEE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 8AF | ST (DFES) | 1.9445 | 1.8795 | 1.7985 | 1.7035 | 1.5945 | 1.4095 | 1.2215 | 0.9965 | 0.7665 | 0.5325 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | Low Road | SKELTON GRANGE | LS1 4HR | ST (DFES) | 7.776 | 7.774 | 7.772 | 7.77 | 7.767 | 7.762 | 7.758 | 7.752 | 7.746 | 7.74 | 7.709 | 7.679 | 7.651 | 7.629 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS1 4BN | ST (DFES) | 18.7039 | 18.7009 | 18.6979 | 18.6939 | 18.6899 | 18.6819 | 18.6739 | 18.6649 | 18.6559 | 18.6459 | 18.5959 | 18.5479 | 18.5039 | 18.4679 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WIBSEY | 11 | 33 | Staygate | SKELTON GRANGE | BD6 3BG | ST (DFES) | 0.62226 | 0.56026 | 0.48326 | 0.39326 | 0.28926 | 0.11326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WITHERNSEA | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU19 2QA | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOODCOCK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 5LL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOODSEATS | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 8QB | ST (DFES) | 2.2207 | 2.1707 | 2.1097 | 2.0377 | 1.9547 | 1.8127 | 1.6687 | 1.4967 | 1.3207 | 1.1427 | 0.20769 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOOLLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 5JE | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WORSBROUGH PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S70 5LY | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WRAWBY | 11 | 33 | Santon | KEADBY | DN20 8SX | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4BL | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YEW GREEN ROAD | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD4 5DD | ST (DFES) | 1.373 | 1.326 | 1.268 | 1.199 | 1.121 | 0.98797 | 0.85197 | 0.68997 | 0.52497 | 0.35597 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YORK ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 6TF | ST (DFES) | 20.7981 | 20.7421 | 20.6721 | 20.5901 | 20.4951 | 20.3361 | 20.1741 | 19.9791 | 19.7811 | 19.5781 | 18.5111 | 17.4731 | 16.5291 | 15.7661 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YORK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 3AZ | ST (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - System Transformation (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ANNFIELD | 66 | 132 | Annfield | STELLA SOUTH | DH9 7XW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BARRACK ROAD | 33 | 132 | Barrack Road | STELLA NORTH | NE4 6DB | LTW (DFES) | 114.625 | 114.433 | 114.233 | 114 | 113.747 | 113.385 | 113.023 | 112.584 | 112.124 | 111.619 | 108.771 | 106.544 | 104.26 | 102.285 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER | 33 | 132 | Blucher | STELLA NORTH | NE15 9SD | LTW (DFES) | 94.462 | 94.052 | 93.533 | 93.134 | 92.724 | 92.042 | 91.344 | 90.536 | 89.769 | 88.93 | 85.004 | 80.985 | 77.239 | 74.175 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD | 33 | 132 | Bowesfield | NORTON | TS18 3HP | LTW (DFES) | 61.841 | 59.812 | 56.971 | 55.788 | 54.922 | 53.455 | 51.887 | 50.326 | 49.341 | 47.853 | 45.195 | 38.897 | 32.437 | 26.799 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CHIRTON GRANGE | 33 | 132 | Chirton Grange | TYNEMOUTH | NE29 8EY | LTW (DFES) | 62.036 | 61.683 | 61.266 | 60.857 | 60.413 | 59.708 | 58.993 | 58.144 | 57.292 | 56.38 | 51.657 | 47.347 | 43.249 | 39.859 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | COALBURNS | 66 | 132 | Coalburns | STELLA SOUTH | NE40 4JP | LTW (DFES) | 69.861 | 67.799 | 64.862 | 63.925 | 63.411 | 62.478 | 61.428 | 60.541 | 60.349 | 59.607 | 61.857 | 59.166 | 56.026 | 53.025 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL | 33 | 132 | Darlington Central | NORTON | DL1 1HG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON NORTH | 33 | 132 | Darlington North | NORTON | DL3 0XE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON | 66 | 132 | Dunston | STELLA NORTH | NE11 9DH | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH | 33 | 132 | Flatworth | TYNEMOUTH | NE29 7FN | LTW (DFES) | 27.32 | 27.166 | 26.987 | 26.791 | 26.572 | 26.218 | 25.861 | 25.434 | 24.999 | 24.544 | 22.14 | 19.957 | 17.916 | 16.252 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH | 33 | 132 | Gosforth | TYNEMOUTH | NE3 1XL | LTW (DFES) | 88.943 | 88.647 | 88.308 | 87.947 | 87.547 | 86.904 | 86.254 | 85.478 | 84.692 | 83.862 | 79.506 | 75.55 | 71.835 | 68.794 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/33KV | 33 | 132 | Harrogate 132/33kV | KNARESBOROUGH | HG1 2LA | LTW (DFES) | 45.918 | 45.419 | 44.768 | 44.339 | 43.926 | 43.261 | 42.572 | 41.788 | 41.069 | 40.237 | 36.551 | 32.675 | 28.897 | 25.683 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE | 33 | 132 | Husthwaite | KNARESBOROUGH | YO61 4PN | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | Leeming Bar_Skeeby | NORTON | DL7 0RL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LINTON | 66 | 132 | Linton | BLYTH 132kV | NE61 5DA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALTON GRID | 66 | 132 | Malton Grid | OSBALDWICK | YO17 6RD | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 132/33kV | 33 | 132 | Melrosegate | OSBALDWICK | YO31 0YB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES | 66 | 132 | North Tees | NORTON | TS23 1PY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE 132/66kV | 66 | 132 | Potter House | SPENNYMOOR | DH1 5FF | LTW (DFES) | 89.328 | 88.29 | 86.864 | 86.094 | 85.426 | 84.352 | 83.229 | 82.011 | 81.006 | 79.749 | 75.13 | 69.539 | 63.923 | 59.077 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSWORTH | 66 | 132 | Ravensworth | STELLA SOUTH | DH3 1RQ | LTW (DFES) | 76.362 | 75.999 | 75.509 | 75.241 | 75.009 | 74.647 | 74.27 | 73.861 | 73.525 | 73.099 | 71.506 | 69.665 | 67.771 | 66.121 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH GRID | 33 | 132 | Scarborough Grid | OSBALDWICK | YO11 2YH | LTW (DFES) | 71.275 | 69.569 | 67.308 | 66.342 | 65.614 | 64.378 | 63.056 | 61.712 | 60.813 | 59.492 | 56.563 | 50.813 | 44.969 | 39.857 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEAL SANDS | 66 | 132 | Seal Sands | SALTHOLME | TS2 1FB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5LJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO | 66 | 132 | Toronto | SPENNYMOOR | DL14 7RJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 3PS | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ATTERCLIFFE | 33 | 132 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3FA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 132/66KV | 66 | 132 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1LR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6NJ | LTW (DFES) | 67.3734 | 66.6554 | 65.5414 | 65.0624 | 64.7574 | 63.9844 | 63.1064 | 62.1634 | 61.4464 | 60.5194 | 56.6454 | 51.6454 | 47.1394 | 43.3374 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEVERLEY 132/33KV | 33 | 132 | Beverley 132/33kV | CREYKE BECK | HU17 0RW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 132/33KV | 33 | 132 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | LTW (DFES) | 9.9206 | 9.6916 | 9.3976 | 9.0876 | 8.7426 | 8.1466 | 7.5336 | 6.8006 | 6.0596 | 5.2926 | 1.2966 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS B | 33 | 132 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1DA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLYTON | 33 | 132 | Blyton | KEADBY | DN21 3NS | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRADFORD | 33 | 132 | Bradford | BRADFORD WEST | BD1 4RF | LTW (DFES) | 99.717 | 99.449 | 99.117 | 98.726 | 98.276 | 97.514 | 96.736 | 95.798 | 94.837 | 93.854 | 88.67 | 83.564 | 78.903 | 75.09 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHAM | 33 | 132 | Bramham | FERRYBRIDGE B | LS24 9NT | LTW (DFES) | 26.0107 | 23.0577 | 18.0607 | 16.9637 | 17.1447 | 16.0507 | 14.4167 | 13.0957 | 13.1357 | 12.0327 | 11.7327 | 5.1597 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRANSHOLME | 33 | 132 | Bransholme | CREYKE BECK | HU7 4ZN | LTW (DFES) | 65.6003 | 64.9713 | 63.9843 | 63.5903 | 63.3643 | 62.7453 | 62.0313 | 61.2763 | 60.7313 | 59.9943 | 57.0353 | 53.0333 | 49.4273 | 46.3613 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | Brighouse 132/33kV | ELLAND | HD6 1PZ | LTW (DFES) | 95.8397 | 95.0337 | 93.7617 | 93.3007 | 93.0777 | 92.3667 | 91.5267 | 90.6557 | 90.0707 | 89.2307 | 86.0787 | 81.4127 | 77.2517 | 73.6947 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 8UX | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER CENTRAL | 33 | 132 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1RE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | Driffield/Beverley Group | CREYKE BECK | YO25 5NW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FEATHERSTONE | 33 | 132 | Featherstone | FERRYBRIDGE B | WF7 6HE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIRLINGTON | 33 | 132 | Girlington | BRADFORD WEST | BD7 2NB | LTW (DFES) | 85.2765 | 85.1145 | 84.9135 | 84.6765 | 84.4045 | 83.9435 | 83.4735 | 82.9065 | 82.3255 | 81.7305 | 78.5955 | 75.5065 | 72.6875 | 70.3815 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 132/33KV | 33 | 132 | Halifax 132/33kV | ELLAND | HX1 1XB | LTW (DFES) | 1.4816 | 1.3926 | 1.2836 | 1.1546 | 1.0076 | 0.75862 | 0.50262 | 0.19162 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HECKMONDWIKE | 33 | 132 | Heckmondwike | SKELTON GRANGE | WF16 9LU | LTW (DFES) | 88.832 | 88.645 | 88.41 | 88.133 | 87.817 | 87.285 | 86.743 | 86.087 | 85.413 | 84.721 | 81.059 | 77.478 | 74.188 | 71.48 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLMFIELD | 33 | 132 | Holmfield | BRADFORD WEST | HX2 9AY | LTW (DFES) | 57.3015 | 57.0055 | 56.6435 | 56.2155 | 55.7275 | 54.8965 | 54.0445 | 53.0135 | 51.9495 | 50.8565 | 45.0795 | 39.3515 | 34.1105 | 29.7825 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 132/33KV | 33 | 132 | Hull East 132/33kV | SALTEND NORTH | HU9 5NL | LTW (DFES) | 8.6627 | 8.3847 | 7.9987 | 7.5637 | 7.0907 | 6.3487 | 5.5827 | 4.6477 | 3.6567 | 2.6087 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL SOUTH | 33 | 132 | Hull South | CREYKE BECK | HU3 5JA | LTW (DFES) | 88.4812 | 88.2242 | 87.8962 | 87.5112 | 87.0732 | 86.3482 | 85.6082 | 84.7142 | 83.7912 | 82.8412 | 77.7812 | 72.9062 | 68.3872 | 64.6412 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL WEST | 33 | 132 | Hull West | CREYKE BECK | HU13 0FA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUMBERSTON | 33 | 132 | Humberston | GRIMSBY WEST | DN36 4AW | LTW (DFES) | 67.5551 | 67.2381 | 66.7631 | 66.4531 | 66.1761 | 65.6561 | 65.1001 | 64.4621 | 63.8751 | 63.2111 | 59.9341 | 56.5281 | 53.3381 | 50.6351 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNNINGLEY | 33 | 132 | Hunningley | WEST MELTON SECTION 3 | S70 3ET | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNSHELF | 66 | 132 | Hunshelf | WEST MELTON SECTION 3 | S36 8WR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IMMINGHAM | 33 | 132 | Immingham | GRIMSBY WEST | DN40 1QT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKHAW LANE | 33 | 132 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8SB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C 2/5 | 33 | 132 | Kirkstall C 2/5 | KIRKSTALL B | LS18 4EL | LTW (DFES) | 81.9502 | 81.8952 | 81.8262 | 81.7452 | 81.6522 | 81.4972 | 81.3392 | 81.1492 | 80.9532 | 80.7522 | 79.6872 | 78.6542 | 77.7032 | 76.9212 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS18 4EL | LTW (DFES) | 106.5525 | 106.0445 | 105.3345 | 104.7715 | 104.2085 | 103.1825 | 102.1065 | 100.8475 | 99.6365 | 98.3305 | 91.7545 | 84.9645 | 78.7445 | 73.5975 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS EAST | 33 | 132 | Leeds East | SKELTON GRANGE | LS9 6ED | LTW (DFES) | 65.9152 | 65.3452 | 64.4792 | 64.0422 | 63.7132 | 62.9782 | 62.1662 | 61.2682 | 60.5222 | 59.6232 | 55.5832 | 50.7942 | 46.4542 | 42.8172 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS NORTH | 33 | 132 | Leeds North | SKELTON GRANGE | LS7 2AU | LTW (DFES) | 107.913 | 107.74 | 107.522 | 107.265 | 106.971 | 106.48 | 105.98 | 105.377 | 104.757 | 104.121 | 100.752 | 97.482 | 94.471 | 91.996 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LINDLEY | 33 | 132 | Lindley | ELLAND | HD3 3NY | LTW (DFES) | 92.5602 | 92.0552 | 91.3182 | 90.8612 | 90.4602 | 89.6552 | 88.7882 | 87.7982 | 86.9052 | 85.8932 | 81.0492 | 75.6962 | 70.8272 | 66.7692 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOW ROAD | 33 | 132 | Low Road | SKELTON GRANGE | LS10 1RH | LTW (DFES) | 1.726 | 1.552 | 1.318 | 1.099 | 0.86602 | 0.45802 | 0.036016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MALLARD WAY | 33 | 132 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MENSTON | 33 | 132 | Menston | BRADFORD WEST | LS29 6BP | LTW (DFES) | 86.9257 | 86.1197 | 84.8177 | 84.4187 | 84.2957 | 83.7287 | 83.0287 | 82.3407 | 81.9777 | 81.3447 | 79.3987 | 75.8247 | 72.6637 | 69.9307 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOSS ROAD | 33 | 132 | Moss Road | GRIMSBY WEST | DN32 0LW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 1/2 | 33 | 132 | Osgodby 1/2 | DRAX | YO8 5HY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 3/4 | 33 | 132 | Osgodby 3/4 | DRAX | YO8 5HY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY | 33 | 132 | Rodley | SKELTON GRANGE | LS13 1PZ | LTW (DFES) | 121.6231 | 120.9541 | 119.9221 | 119.4631 | 119.1591 | 118.4091 | 117.5641 | 116.6491 | 115.9381 | 115.0361 | 111.2011 | 106.3411 | 101.9611 | 98.2741 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | LTW (DFES) | 81.2628 | 81.0218 | 80.7128 | 80.3788 | 80.0078 | 79.3728 | 78.7218 | 77.9398 | 77.1438 | 76.3198 | 71.9978 | 67.7268 | 63.8058 | 60.5728 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTEND 132/33KV | 33 | 132 | Saltend 132/33kV | SALTEND NORTH | HU12 8EY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SANTON | 33 | 132 | Santon | KEADBY | DN16 1XP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE NORTH | 33 | 132 | Scunthorpe North | KEADBY | DN15 8GN | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE SOUTH | 33 | 132 | Scunthorpe South | KEADBY | DN16 1BD | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILSDEN | 33 | 132 | Silsden | BRADFORD WEST | BD20 0ND | LTW (DFES) | 0 | 52.4267 | 50.3557 | 49.4447 | 48.9047 | 47.5237 | 45.8797 | 44.0277 | 42.4497 | 40.3687 | 30.8127 | 19.0547 | 7.9167 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EL | LTW (DFES) | 59.6804 | 59.3204 | 58.8234 | 58.4534 | 58.0944 | 57.4114 | 56.6864 | 55.8354 | 55.0204 | 54.1304 | 49.6864 | 44.9354 | 40.6054 | 36.9834 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAYGATE | 33 | 132 | Staygate | SKELTON GRANGE | BD6 1YA | LTW (DFES) | 116.0447 | 115.8307 | 115.5667 | 115.2547 | 114.8957 | 114.2887 | 113.6687 | 112.9217 | 112.1557 | 111.3727 | 107.2417 | 103.1727 | 99.4577 | 96.4197 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNHILL 132KV | 33 | 132 | Thornhill 132kV | ELLAND | WF13 3JQ | LTW (DFES) | 19.6877 | 18.7817 | 17.3887 | 16.7357 | 16.2807 | 15.2147 | 14.0197 | 12.7137 | 11.6677 | 10.3627 | 4.6507 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7AL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD NORTH | 33 | 132 | Wakefield North | SKELTON GRANGE | WF1 3HN | LTW (DFES) | 80.2544 | 79.1744 | 77.4344 | 76.8104 | 76.5214 | 75.6184 | 74.5464 | 73.4494 | 72.7434 | 71.6844 | 67.7484 | 62.0364 | 56.8144 | 52.2834 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST MELTON | 66 | 132 | West Melton | WEST MELTON SECTION 3 | S63 6EZ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHINMOOR | 33 | 132 | Whinmoor | FERRYBRIDGE B | LS14 2DG | LTW (DFES) | 113.4923 | 112.3613 | 110.5403 | 109.9703 | 109.7813 | 108.9643 | 107.9613 | 106.9703 | 106.4293 | 105.5113 | 102.6103 | 97.4513 | 92.8833 | 88.9423 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOLD NEWTON | 33 | 132 | Wold Newton | KEADBY | DN37 0SW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4JJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ACKLAM | 11 | 33 | Bowesfield | NORTON | TS5 7LD | LTW (DFES) | 15.7694 | 15.6704 | 15.5504 | 15.4084 | 15.2474 | 14.9834 | 14.7174 | 14.3964 | 14.0684 | 13.7304 | 11.9364 | 10.2914 | 8.7794 | 7.5584 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AMBERTON ROAD | 11 | 66 | Hartmoor | HARTMOOR | TS24 8PQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ANNFIELD 66/20KV | 20 | 66 | Annfield | STELLA SOUTH | DH9 7XW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ASHINGTON | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE63 8UJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE FORREST | 11 | 33 | Darlington North | NORTON | DL1 3NL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | Darlington North | NORTON | DL5 6HY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BARDEN FRIAR | 20 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5JR | LTW (DFES) | 7.592 | 7.584 | 7.573 | 7.562 | 7.549 | 7.532 | 7.514 | 7.493 | 7.469 | 7.443 | 7.294 | 7.179 | 7.058 | 6.948 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BEDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 1AH | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BELMONT | 11 | 66 | Potter House | SPENNYMOOR | DH1 2HL | LTW (DFES) | 2.8215 | 2.7335 | 2.6225 | 2.4935 | 2.3495 | 2.1305 | 1.9085 | 1.6395 | 1.3595 | 1.0615 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENSHAM | 11 | 66 | Dunston | STELLA NORTH | NE8 2XY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.941 | 11.747 | 11.544 | 10.45 | 9.485 | 8.573 | 7.823 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENTON SQUARE | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE12 9SR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENWELL | 11 | 66 | Dunston | STELLA NORTH | NE4 8XQ | LTW (DFES) | 12.123 | 12.039 | 11.946 | 11.837 | 11.713 | 11.515 | 11.316 | 11.075 | 10.829 | 10.571 | 9.186 | 7.952 | 6.795 | 5.849 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | North Tees | NORTON | TS23 2AL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BILLY MILL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE29 8LP | LTW (DFES) | 17.3679 | 17.2979 | 17.2169 | 17.1209 | 17.0119 | 16.8339 | 16.6539 | 16.4369 | 16.2159 | 15.9869 | 14.7689 | 13.6569 | 12.6309 | 11.8019 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | LTW (DFES) | 32.6462 | 32.5932 | 32.5272 | 32.4502 | 32.3622 | 32.2222 | 32.0812 | 31.9102 | 31.7332 | 31.5492 | 30.5622 | 29.6742 | 28.8422 | 28.1582 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | LTW (DFES) | 24.2612 | 24.2252 | 24.1832 | 24.1332 | 24.0772 | 23.9902 | 23.9032 | 23.7982 | 23.6882 | 23.5732 | 22.9462 | 22.4042 | 21.8842 | 21.4512 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLAYDON BURN | 11 | 66 | Dunston | STELLA NORTH | NE21 4BG | LTW (DFES) | 1.949 | 1.869 | 1.772 | 1.659 | 1.532 | 1.339 | 1.144 | 0.91 | 0.666 | 0.409 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER 33/11KV | 11 | 33 | Blucher | STELLA NORTH | NE15 9SB | LTW (DFES) | 14.5182 | 14.4452 | 14.3602 | 14.2612 | 14.1472 | 13.9602 | 13.7702 | 13.5432 | 13.3102 | 13.0702 | 11.7992 | 10.6272 | 9.5532 | 8.6882 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOLDON DOWNHILL | 20 | 66 | West Boldon | WEST BOLDON | NE36 0AS | LTW (DFES) | 19.3145 | 19.2585 | 19.1905 | 19.1115 | 19.0205 | 18.8715 | 18.7215 | 18.5415 | 18.3565 | 18.1655 | 17.1555 | 16.2275 | 15.3755 | 14.6875 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | YO51 9NS | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 33/11KV | 11 | 33 | Bowesfield | NORTON | TS18 3HR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 66/11KV | 11 | 66 | North Tees | NORTON | TS23 1PX | LTW (DFES) | 39.3121 | 39.2621 | 39.2001 | 39.1271 | 39.0471 | 38.9251 | 38.8031 | 38.6551 | 38.5021 | 38.3391 | 37.4441 | 36.6921 | 35.9581 | 35.3401 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BRANCEPETH | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL15 0TW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BREAMISH STREET | 11 | 66 | West Boldon | WEST BOLDON | NE1 2BL | LTW (DFES) | 22.466 | 22.424 | 22.38 | 22.329 | 22.272 | 22.187 | 22.101 | 21.998 | 21.89 | 21.775 | 21.137 | 20.608 | 20.088 | 19.649 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BRENDA TRADING | 11 | 66 | Hartmoor | HARTMOOR | TS25 1PD | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CAMPLESHON ROAD | 11 | 33 | Melrosegate | OSBALDWICK | YO23 1HZ | LTW (DFES) | 0.4177 | 0.3277 | 0.2297 | 0.1147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARLEY HILL | 11 | 66 | West Boldon | WEST BOLDON | SR5 1SG | LTW (DFES) | 19.569 | 19.472 | 19.354 | 19.217 | 19.063 | 18.821 | 18.578 | 18.285 | 17.983 | 17.666 | 15.949 | 14.454 | 13.03 | 11.854 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARLIN HOW T3 T4 | 11 | 66 | Lackenby | LACKENBY | TS13 4DL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARR HILL | 11 | 66 | West Boldon | WEST BOLDON | NE10 9SY | LTW (DFES) | 20.0069 | 19.9009 | 19.7709 | 19.6169 | 19.4439 | 19.1649 | 18.8829 | 18.5439 | 18.1949 | 17.8339 | 15.8999 | 14.1589 | 12.5369 | 11.2149 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CATTERICK CAMP | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL9 3HE | LTW (DFES) | 8.633 | 8.502 | 8.341 | 8.153 | 7.94 | 7.607 | 7.266 | 6.847 | 6.405 | 5.931 | 3.334 | 1.028 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CLOSE | 11 | 66 | Dunston | STELLA NORTH | NE1 3NB | LTW (DFES) | 12.778 | 12.708 | 12.646 | 12.575 | 12.5 | 12.402 | 12.304 | 12.186 | 12.059 | 11.912 | 11.052 | 10.452 | 9.784 | 9.181 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CONEYTHORPE | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG5 0RZ | LTW (DFES) | 6.8396 | 6.7726 | 6.6946 | 6.6046 | 6.5026 | 6.3466 | 6.1866 | 5.9936 | 5.7926 | 5.5776 | 4.3976 | 3.3786 | 2.3906 | 1.5546 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CONSETT | 20 | 66 | Annfield | STELLA SOUTH | DH8 7ND | LTW (DFES) | 7.742 | 7.607 | 7.438 | 7.241 | 7.02 | 6.677 | 6.33 | 5.909 | 5.471 | 5.008 | 2.486 | 0.29 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CORPORATION STREET | 11 | 33 | Barrack Road | STELLA NORTH | NE4 5SS | LTW (DFES) | 19.5775 | 19.5445 | 19.5115 | 19.4725 | 19.4285 | 19.3635 | 19.2985 | 19.2185 | 19.1365 | 19.0485 | 18.5605 | 18.1555 | 17.7565 | 17.4205 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | COWTON | 11 | 33 | Darlington Central | NORTON | DL6 2NF | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLEY | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 2PP | LTW (DFES) | 9.511 | 9.478 | 9.439 | 9.395 | 9.346 | 9.275 | 9.204 | 9.117 | 9.026 | 8.926 | 8.363 | 7.911 | 7.451 | 7.051 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 132/6KV | 6 | 132 | Darlington 132/6kV | NORTON | DL1 1SW | LTW (DFES) | 0 | 29.7434 | 29.6954 | 29.6394 | 29.5764 | 29.4794 | 29.3814 | 29.2624 | 29.1394 | 29.0094 | 28.3004 | 27.6914 | 27.1044 | 26.6134 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1SW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1HG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON EAST | 11 | 33 | Darlington Central | NORTON | DL1 4NP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON WEST | 11 | 33 | Darlington North | NORTON | DL3 9QG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DENWICK | 20 | 66 | Linton | BLYTH 132kV | NE66 3RG | LTW (DFES) | 5.934 | 5.771 | 5.564 | 5.324 | 5.06 | 4.677 | 4.287 | 3.811 | 3.303 | 2.751 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/11KV | 11 | 66 | Dunston | STELLA NORTH | NE11 9DH | LTW (DFES) | 1.3613 | 1.3123 | 1.2523 | 1.1823 | 1.1043 | 0.98928 | 0.87328 | 0.73328 | 0.58728 | 0.43128 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/20KV | 20 | 66 | Dunston | STELLA NORTH | NE11 9DH | LTW (DFES) | 11.998 | 11.915 | 11.815 | 11.697 | 11.564 | 11.354 | 11.142 | 10.886 | 10.623 | 10.349 | 8.869 | 7.561 | 6.328 | 5.314 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DURHAM EAST | 11 | 66 | Potter House | SPENNYMOOR | DH1 5SU | LTW (DFES) | 22.1118 | 22.0618 | 21.9978 | 21.9238 | 21.8438 | 21.7388 | 21.6328 | 21.5048 | 21.3678 | 21.2148 | 20.3278 | 19.6808 | 18.9798 | 18.3518 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EASTFIELD | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 3BY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.4669 | 21.2019 | 20.9229 | 19.4289 | 18.0619 | 16.7849 | 15.7289 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EASTGATE CEMENT | 20 | 66 | Toronto | SPENNYMOOR | DL13 2LA | LTW (DFES) | 11.653 | 11.622 | 11.583 | 11.538 | 11.49 | 11.422 | 11.354 | 11.271 | 11.183 | 11.087 | 10.539 | 10.117 | 9.676 | 9.289 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | Barrack Road | STELLA NORTH | NE5 4JQ | LTW (DFES) | 22.7119 | 22.6569 | 22.6009 | 22.5339 | 22.4609 | 22.3509 | 22.2409 | 22.1069 | 21.9689 | 21.8199 | 20.9959 | 20.3139 | 19.6419 | 19.0749 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ELVINGTON | 11 | 33 | Melrosegate | OSBALDWICK | YO41 4DY | LTW (DFES) | 0.9457 | 0.9197 | 0.8927 | 0.8607 | 0.8257 | 0.7757 | 0.7257 | 0.6647 | 0.6007 | 0.5297 | 0.1317 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FARADAY STREET | 11 | 66 | North Tees | NORTON | TS1 4JG | LTW (DFES) | 13.1998 | 13.0878 | 12.9568 | 12.8038 | 12.6328 | 12.3748 | 12.1138 | 11.8008 | 11.4748 | 11.1298 | 9.2338 | 7.6378 | 6.0828 | 4.7798 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | Blyth 66kV | BLYTH 66KV | NE3 2SW and NE13 6BH | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FISHBURN | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | TS29 6JQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH CENTRAL | 11 | 33 | Flatworth | TYNEMOUTH | NE29 7SH | LTW (DFES) | 30.6837 | 30.6347 | 30.5807 | 30.5177 | 30.4467 | 30.3377 | 30.2267 | 30.0937 | 29.9557 | 29.8107 | 29.0187 | 28.3377 | 27.6837 | 27.1407 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FOSS ISLANDS | 11 | 33 | Melrosegate | OSBALDWICK | YO31 7US | LTW (DFES) | 1.3597 | 1.2277 | 1.0977 | 0.9457 | 0.7777 | 0.5287 | 0.2777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FOSSWAY 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE6 4AN | LTW (DFES) | 14.3829 | 14.2859 | 14.1799 | 14.0539 | 13.9129 | 13.6889 | 13.4629 | 13.1899 | 12.9099 | 12.6159 | 11.0339 | 9.6349 | 8.3169 | 7.2349 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FYLANDS BRIDGE | 11 | 66 | Toronto | SPENNYMOOR | DL14 9TA | LTW (DFES) | 9.969 | 9.866 | 9.739 | 9.589 | 9.421 | 9.156 | 8.887 | 8.563 | 8.226 | 7.872 | 5.953 | 4.258 | 2.646 | 1.304 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GALE LANE | 11 | 33 | Poppleton | POPPLETON | YO24 3AF | LTW (DFES) | 7.761 | 7.685 | 7.597 | 7.494 | 7.375 | 7.177 | 6.976 | 6.734 | 6.488 | 6.234 | 4.895 | 3.642 | 2.502 | 1.587 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GARWOOD STREET | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 5DQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.7946 | 20.5366 | 20.2596 | 18.7266 | 17.4676 | 16.2196 | 15.1626 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD CENTRAL | 11 | 33 | Barrack Road | STELLA NORTH | NE8 1HB | LTW (DFES) | 16.9178 | 16.8738 | 16.8208 | 16.7588 | 16.6918 | 16.5958 | 16.5008 | 16.3848 | 16.2628 | 16.1308 | 15.3838 | 14.8008 | 14.2018 | 13.6828 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD EAST | 11 | 66 | West Boldon | WEST BOLDON | NE8 3AH | LTW (DFES) | 22.622 | 22.614 | 22.604 | 22.594 | 22.582 | 22.567 | 22.552 | 22.533 | 22.513 | 22.491 | 22.364 | 22.271 | 22.17 | 22.082 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE3 1RR | LTW (DFES) | 30.505 | 30.465 | 30.423 | 30.373 | 30.318 | 30.233 | 30.148 | 30.045 | 29.939 | 29.825 | 29.205 | 28.678 | 28.168 | 27.742 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GRANGETOWN | 11 | 66 | Lackenby | LACKENBY | TS6 7AS | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GREATHAM | 11 | 132 | Greatham | SALTHOLME | TS25 2DD | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | Lackenby | LACKENBY | TS14 6GQ | LTW (DFES) | 5.874 | 5.742 | 5.576 | 5.381 | 5.164 | 4.828 | 4.487 | 4.076 | 3.648 | 3.197 | 0.73402 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARLOW GREEN | 11 | 66 | West Boldon | WEST BOLDON | NE9 6NT | LTW (DFES) | 14.4321 | 14.3401 | 14.2281 | 14.0961 | 13.9461 | 13.7041 | 13.4601 | 13.1671 | 12.8651 | 12.5531 | 10.8821 | 9.3751 | 7.9731 | 6.8311 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARMIRE BRIDGE | 20 | 66 | Toronto | SPENNYMOOR | DL12 8QJ | LTW (DFES) | 8.337 | 8.252 | 8.146 | 8.022 | 7.888 | 7.697 | 7.504 | 7.271 | 7.023 | 6.753 | 5.226 | 4.022 | 2.782 | 1.7 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARRATON | 11 | 132 | Harraton | STELLA SOUTH | NE38 9BZ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.868 | 36.661 | 36.442 | 35.238 | 34.229 | 33.243 | 32.414 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/11KV | 11 | 132 | Harrogate 132/11kV | KNARESBOROUGH | HG1 2BN | LTW (DFES) | 27.66 | 27.476 | 27.263 | 27.013 | 26.733 | 26.303 | 25.866 | 25.335 | 24.78 | 24.189 | 20.944 | 18.144 | 15.427 | 13.126 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE WEST | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 0QB | LTW (DFES) | 32.584 | 32.534 | 32.476 | 32.408 | 32.334 | 32.222 | 32.108 | 31.971 | 31.826 | 31.67 | 30.805 | 30.082 | 29.366 | 28.751 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARTMOOR 66/20KV | 20 | 66 | Hartmoor | HARTMOOR | TS27 3BL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HAWTHORN PIT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 9NX | LTW (DFES) | 10.444 | 10.311 | 10.149 | 9.957 | 9.742 | 9.401 | 9.056 | 8.639 | 8.208 | 7.758 | 5.323 | 3.165 | 1.124 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | Melrosegate | OSBALDWICK | YO31 8FZ | LTW (DFES) | 0.012716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN | 6 | 66 | West Boldon | WEST BOLDON | NE31 1BD | LTW (DFES) | 0 | 4.8608 | 4.8378 | 4.8098 | 4.7798 | 4.7338 | 4.6878 | 4.6318 | 4.5748 | 4.5128 | 4.1738 | 3.8908 | 3.6138 | 3.3808 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN WEST | 11 | 66 | West Boldon | WEST BOLDON | NE31 1NA | LTW (DFES) | 0.0056837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEDWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE32 4SW | LTW (DFES) | 0.38329 | 0.32829 | 0.26429 | 0.18829 | 0.10129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEIGHINGTON | 11 | 33 | Darlington North | NORTON | DL5 6JW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEXHAM | 20 | 66 | Coalburns | STELLA SOUTH | NE46 4NT | LTW (DFES) | 28.0159 | 27.9429 | 27.8509 | 27.7439 | 27.6239 | 27.4439 | 27.2599 | 27.0359 | 26.7979 | 26.5419 | 25.1239 | 23.9139 | 22.7189 | 21.6869 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HIGH BARMSTON | 11 | 66 | West Boldon | WEST BOLDON | NE38 8QA | LTW (DFES) | 20.752 | 20.684 | 20.602 | 20.507 | 20.4 | 20.236 | 20.071 | 19.872 | 19.666 | 19.449 | 18.262 | 17.248 | 16.27 | 15.456 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HIGH FLATTS | 11 | 66 | Potter House | SPENNYMOOR | DH2 2LR | LTW (DFES) | 21.3662 | 21.2652 | 21.1402 | 20.9932 | 20.8282 | 20.5682 | 20.3042 | 19.9862 | 19.6552 | 19.3082 | 17.4252 | 15.7642 | 14.1832 | 12.8662 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HOUGHTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | DH4 5HP | LTW (DFES) | 3.8281 | 3.7431 | 3.6391 | 3.5171 | 3.3791 | 3.1601 | 2.9401 | 2.6741 | 2.3991 | 2.1121 | 0.56214 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HOWDON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 0JX | LTW (DFES) | 4.3505 | 4.3265 | 4.2995 | 4.2665 | 4.2305 | 4.1725 | 4.1135 | 4.0425 | 3.9695 | 3.8935 | 3.4865 | 3.1225 | 2.7825 | 2.5035 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUNTINGTON NEW LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO32 9TA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | Husthwaite | KNARESBOROUGH | YO61 4PN | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | JARROW | 11 | 33 | South Shields | SOUTH SHIELDS | NE32 5LD | LTW (DFES) | 18.4196 | 18.3976 | 18.3726 | 18.3436 | 18.3116 | 18.2616 | 18.2116 | 18.1516 | 18.0886 | 18.0226 | 17.6596 | 17.3526 | 17.0546 | 16.8046 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KENTON | 11 | 33 | Blucher | STELLA NORTH | NE3 4UP | LTW (DFES) | 3.2091 | 3.1451 | 3.0741 | 2.9901 | 2.8941 | 2.7371 | 2.5791 | 2.3891 | 2.1941 | 1.9921 | 0.9181 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KIELDER | 20 | 33 | Spadeadam 33kV | SPADEADAM | NE48 1BH | LTW (DFES) | 4.056 | 4.048 | 4.037 | 4.024 | 4.011 | 3.993 | 3.975 | 3.952 | 3.928 | 3.902 | 3.746 | 3.63 | 3.505 | 3.393 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KILLINGWORTH | 11 | 33 | Gosforth | TYNEMOUTH | NE12 6QQ | LTW (DFES) | 11.599 | 11.541 | 11.475 | 11.398 | 11.309 | 11.166 | 11.021 | 10.847 | 10.668 | 10.483 | 9.495 | 8.6 | 7.771 | 7.098 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KIRBYMOORSIDE | 11 | 66 | Malton Grid | OSBALDWICK | YO62 6EZ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LINTON 66/20KV | 20 | 66 | Linton | BLYTH 132kV | NE61 3AX | LTW (DFES) | 7.383 | 7.325 | 7.251 | 7.165 | 7.069 | 6.918 | 6.764 | 6.577 | 6.379 | 6.167 | 5.011 | 3.991 | 3.005 | 2.162 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LONGBENTON | 11 | 33 | Gosforth | TYNEMOUTH | NE7 7LR | LTW (DFES) | 19.5872 | 19.5132 | 19.4292 | 19.3302 | 19.2182 | 19.0352 | 18.8502 | 18.6272 | 18.3992 | 18.1632 | 16.9052 | 15.7602 | 14.7022 | 13.8452 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LOW SPENNYMOOR | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL16 7RS | LTW (DFES) | 8.026 | 7.966 | 7.893 | 7.806 | 7.709 | 7.554 | 7.397 | 7.207 | 7.01 | 6.804 | 5.691 | 4.698 | 3.76 | 2.982 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LYNEMOUTH | 20 | 66 | Linton | BLYTH 132kV | NE61 5XH | LTW (DFES) | 6.078 | 6.064 | 6.047 | 6.027 | 6.004 | 5.967 | 5.929 | 5.883 | 5.834 | 5.783 | 5.506 | 5.253 | 5.013 | 4.811 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MADDISON STREET | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE24 1HD | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALLEABLE | 11 | 66 | North Tees | NORTON | TS18 2NR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6189 | 1.4199 | 1.2039 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALTON | 11 | 66 | Malton Grid | OSBALDWICK | YO17 6BT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MEADOWFIELD | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH7 8ER | LTW (DFES) | 0.903 | 0.866 | 0.821 | 0.769 | 0.711 | 0.625 | 0.539 | 0.435 | 0.326 | 0.208 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 33/11KV | 11 | 33 | Melrosegate | OSBALDWICK | YO31 0YB | LTW (DFES) | 1.6757 | 1.6227 | 1.5657 | 1.4977 | 1.4207 | 1.2997 | 1.1767 | 1.0287 | 0.8757 | 0.7157 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MILLBANK LANE | 11 | 33 | Bowesfield | NORTON | TS17 0AX | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.1672 | 18.9062 | 18.6342 | 17.1812 | 15.8722 | 14.6512 | 13.6562 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MONKSEATON | 11 | 33 | Chirton Grange | TYNEMOUTH | NE25 9AF | LTW (DFES) | 19.4472 | 19.3292 | 19.1952 | 19.0372 | 18.8592 | 18.5762 | 37.529 | 37.183 | 36.827 | 36.452 | 34.429 | 32.635 | 30.939 | 29.537 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MOOR MONKTON PUMPS | 11 | 33 | Poppleton | POPPLETON | YO30 1BY | LTW (DFES) | 13.4109 | 13.3989 | 13.3849 | 13.3689 | 13.3509 | 13.3219 | 13.2939 | 13.2589 | 13.2229 | 13.1839 | 12.9699 | 12.7849 | 12.6049 | 12.4519 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MORPETH | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE61 6JH | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MOUNT ROAD | 11 | 33 | Offerton | OFFERTON | SR4 7LJ | LTW (DFES) | 24.1072 | 24.0092 | 23.8922 | 23.7552 | 23.6042 | 23.3742 | 23.1432 | 22.8652 | 22.5762 | 22.2692 | 20.5822 | 19.1672 | 17.7842 | 16.6232 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWBURN HAUGH | 11 | 132 | Newburn Haugh | STELLA NORTH | NE15 8SF | LTW (DFES) | 20.4544 | 20.4254 | 20.3934 | 20.3564 | 20.3134 | 20.2454 | 20.1764 | 20.0944 | 20.0094 | 19.9204 | 19.4454 | 19.0204 | 18.6224 | 18.2974 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWBY | 11 | 33 | Scarborough Grid | OSBALDWICK | YO12 6NL | LTW (DFES) | 0.22287 | 0.15087 | 0.072868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWCASTLE AIRPORT | 11 | 33 | Blucher | STELLA NORTH | NE13 8DF | LTW (DFES) | 27.1413 | 27.0913 | 27.0303 | 26.9593 | 26.8783 | 26.7463 | 26.6133 | 26.4513 | 26.2833 | 26.1063 | 25.1603 | 24.2983 | 23.4893 | 22.8193 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | Darlington North | NORTON | DL5 6EA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH STREET | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 1DU | LTW (DFES) | 1.4264 | 1.3334 | 1.2504 | 1.1524 | 1.0454 | 0.8864 | 0.7264 | 0.5314 | 0.3274 | 0.1014 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T1 T2 | 11 | 66 | North Tees | NORTON | TS23 1PX | LTW (DFES) | 22.3494 | 22.3074 | 22.2584 | 22.2024 | 22.1444 | 22.0764 | 22.0094 | 21.9274 | 21.8374 | 21.7324 | 21.0904 | 20.6894 | 20.2064 | 19.7514 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T3 T4 | 11 | 66 | North Tees | NORTON | TS23 1PY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5027 | 8.3407 | 8.1637 | 7.1537 | 6.3867 | 5.5837 | 4.8797 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTHALLERTON | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 0QE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTON 132/11KV | 11 | 132 | Norton 132/11kV | NORTON | TS21 1EG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | OATLANDS | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 8BY | LTW (DFES) | 18.3098 | 18.2448 | 18.1698 | 18.0808 | 17.9798 | 17.8218 | 17.6608 | 17.4658 | 17.2618 | 17.0468 | 15.8788 | 14.8438 | 13.8568 | 13.0288 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | OFFERTON 33/11KV | 11 | 33 | Offerton | OFFERTON | SR4 9NR | LTW (DFES) | 26.6058 | 26.5198 | 26.4158 | 26.2928 | 26.1528 | 25.9238 | 25.6938 | 25.4168 | 25.1328 | 24.8388 | 23.2748 | 21.8488 | 20.5308 | 19.4628 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PALLION TRADING | 11 | 33 | Offerton | OFFERTON | SR4 6SN | LTW (DFES) | 13.6238 | 13.5438 | 13.4468 | 13.3328 | 13.2068 | 13.0128 | 12.8168 | 12.5818 | 12.3378 | 12.0798 | 10.6738 | 9.4738 | 8.3148 | 7.3498 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2HR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE WEST | 11 | 66 | Hartmoor | HARTMOOR | DH6 2RA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PILGRIM | 11 | 33 | Barrack Road | STELLA NORTH | NE1 2LA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7132 | 3.6612 | 3.5992 | 3.2232 | 2.9842 | 2.7002 | 2.4332 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | Potter House | SPENNYMOOR | DH1 5FF | LTW (DFES) | 4.536 | 4.428 | 4.294 | 4.137 | 3.959 | 3.675 | 3.387 | 3.039 | 2.678 | 2.301 | 0.27005 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | Potter House | SPENNYMOOR | DH1 5FF | LTW (DFES) | 26.2342 | 26.2142 | 26.1892 | 26.1602 | 26.1282 | 26.0822 | 26.0362 | 25.9812 | 25.9222 | 25.8582 | 25.5002 | 25.2132 | 24.9212 | 24.6692 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PRISSICK | 11 | 66 | Lackenby | LACKENBY | TS4 3SG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSCAR | 11 | 33 | Scarborough Grid | OSBALDWICK | YO13 0LZ | LTW (DFES) | 10.024 | 10.013 | 10.003 | 9.992 | 9.979 | 9.961 | 9.942 | 9.918 | 9.894 | 9.867 | 9.719 | 9.596 | 9.474 | 9.368 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAWCLIFFE LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO30 5SW | LTW (DFES) | 0.8717 | 0.7927 | 0.7077 | 0.6077 | 0.4957 | 0.3167 | 0.1357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | REDCAR | 11 | 66 | Lackenby | LACKENBY | TS10 2PA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RESERVOIR | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE22 5QP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T1 | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL10 5BJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T2 | 11 | 33 | Darlington North | NORTON | DL10 5BJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RIPON | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG4 1QE | LTW (DFES) | 14.4129 | 14.2869 | 14.1419 | 17.929 | 17.74 | 17.457 | 17.171 | 16.822 | 16.456 | 16.063 | 13.883 | 12.052 | 10.243 | 8.695 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RISE CARR | 6 | 33 | Darlington North | NORTON | DL3 0RP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ROMANBY | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 8HP | LTW (DFES) | 9.9811 | 9.9371 | 9.8831 | 9.8181 | 9.7441 | 9.6221 | 9.4971 | 9.3451 | 9.1871 | 9.0231 | 8.1481 | 7.3311 | 6.5741 | 5.9481 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RUDBY | 11 | 33 | Bowesfield | NORTON | TS15 0JT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 2YH | LTW (DFES) | 2.209 | 2.082 | 1.956 | 1.809 | 1.643 | 1.383 | 1.12 | 0.79902 | 0.46602 | 0.10902 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEGHILL | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 7EY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | Husthwaite | KNARESBOROUGH | YO7 3NT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEVERUS HILL | 11 | 33 | Poppleton | POPPLETON | YO26 4RR | LTW (DFES) | 0.78257 | 0.71057 | 0.63157 | 0.53857 | 0.43457 | 0.26657 | 0.097571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SHERIFF HUTTON | 11 | 66 | Malton Grid | OSBALDWICK | YO60 6QN | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SHOTTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2EL | LTW (DFES) | 1.3672 | 1.2982 | 1.2112 | 1.1092 | 0.99517 | 0.81717 | 0.63717 | 0.42017 | 0.19417 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SIMONSIDE | 11 | 33 | South Shields | SOUTH SHIELDS | NE34 9PD | LTW (DFES) | 13.2171 | 13.1621 | 13.0971 | 13.0211 | 12.9351 | 12.7981 | 12.6601 | 12.4931 | 12.3221 | 12.1441 | 11.1851 | 10.3321 | 9.5321 | 8.8771 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SKELDERGATE | 11 | 33 | Poppleton | POPPLETON | YO1 6HN | LTW (DFES) | 2.1149 | 2.0569 | 2.0029 | 1.9399 | 1.8709 | 1.7759 | 1.6799 | 1.5639 | 1.4409 | 1.3049 | 0.52488 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SKERNESIDE | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL5 6JH | LTW (DFES) | 0.30462 | 0.21262 | 0.10262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENCERBECK | 11 | 66 | Lackenby | LACKENBY | TS3 8TE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5JX | LTW (DFES) | 0.73967 | 0.64867 | 0.53567 | 0.40467 | 0.25667 | 0.027669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STARBECK | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 7PT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STOKESLEY | 11 | 33 | Bowesfield | NORTON | TS9 5HS | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STONEY CUT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 8RQ | LTW (DFES) | 15.8942 | 15.8072 | 15.6982 | 15.5722 | 15.4292 | 15.2032 | 14.9752 | 14.6992 | 14.4122 | 14.1112 | 12.4812 | 11.0402 | 9.6692 | 8.5282 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T1 T2 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | LTW (DFES) | 21.0393 | 20.9513 | 20.8473 | 20.7263 | 20.5963 | 20.4183 | 20.2393 | 20.0233 | 19.7943 | 19.5423 | 18.0993 | 17.0153 | 15.8713 | 14.8673 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T5 T6 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | LTW (DFES) | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.799 | 22.799 | 22.798 | 22.798 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TANFIELD | 11 | 66 | Annfield | STELLA SOUTH | DH9 9DB | LTW (DFES) | 0.60615 | 0.52715 | 0.42815 | 0.31115 | 0.18015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEAM VALLEY | 20 | 66 | Ravensworth | STELLA SOUTH | NE11 0SX | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.0411 | 44.9351 | 44.8141 | 44.0961 | 43.6101 | 43.0581 | 42.5531 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | Seal Sands | SALTHOLME | TS23 3NF | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEMPLE PARK | 11 | 66 | West Boldon | WEST BOLDON | NE34 8TH | LTW (DFES) | 20.0884 | 20.0004 | 19.8954 | 19.7714 | 19.6304 | 19.3994 | 19.1674 | 18.8874 | 18.6014 | 18.3054 | 16.7324 | 15.2954 | 13.9704 | 12.8994 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | THIRSK | 11 | 33 | Leeming Bar_Skeeby | NORTON | YO7 4NH | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | THORNTON DALE | 11 | 66 | Malton Grid | OSBALDWICK | YO18 7SJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO 66/20KV | 20 | 66 | Toronto | SPENNYMOOR | DL14 7RJ | LTW (DFES) | 8.17 | 8.059 | 7.919 | 7.757 | 7.576 | 7.306 | 7.033 | 6.702 | 6.356 | 5.986 | 3.942 | 2.231 | 0.544 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TUNSTALL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR3 2BT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.9449 | 25.6029 | 25.2479 | 23.3599 | 21.6439 | 20.0559 | 18.7689 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE30 1JG | LTW (DFES) | 19.7215 | 19.6165 | 19.5015 | 19.3675 | 19.2175 | 18.9875 | 18.7565 | 18.4775 | 18.1895 | 17.8825 | 16.2055 | 14.7825 | 13.4025 | 12.2505 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | UNIVERSITY | 11 | 33 | Barrack Road | STELLA NORTH | NE2 4PZ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5417 | 10.4757 | 10.4027 | 9.9897 | 9.6707 | 9.3417 | 9.0547 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | URLAY NOOK | 11 | 33 | Bowesfield | NORTON | TS16 0QB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | USWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE37 3HY | LTW (DFES) | 21.62 | 21.581 | 21.535 | 21.481 | 21.42 | 21.324 | 21.228 | 21.112 | 20.992 | 20.867 | 20.189 | 19.597 | 19.034 | 18.57 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WALKER | 11 | 66 | West Boldon | WEST BOLDON | NE6 3PZ | LTW (DFES) | 14.6299 | 14.5459 | 14.4519 | 14.3409 | 14.2149 | 14.0139 | 13.8109 | 13.5659 | 13.3149 | 13.0529 | 11.6489 | 10.3939 | 9.2189 | 8.2609 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WANSBECK | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE22 7DH | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WARDLEY | 6 | 66 | West Boldon | WEST BOLDON | NE31 1LP | LTW (DFES) | 0 | 15.7294 | 15.6754 | 15.6124 | 15.5404 | 15.4274 | 15.3124 | 15.1744 | 15.0324 | 14.8844 | 14.0904 | 13.3834 | 12.7194 | 12.1764 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WARKWORTH | 20 | 66 | Linton | BLYTH 132kV | NE65 0YD | LTW (DFES) | 6.429 | 6.309 | 6.156 | 5.979 | 5.781 | 5.483 | 5.179 | 4.809 | 4.416 | 3.993 | 1.645 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WENSLEYDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5ED | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST HARTFORD | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 3JP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST SOUTHWICK | 11 | 66 | West Boldon | WEST BOLDON | SR5 3TX | LTW (DFES) | 20.656 | 20.607 | 20.55 | 20.482 | 20.405 | 20.286 | 20.165 | 20.019 | 19.869 | 19.712 | 18.864 | 18.121 | 17.416 | 16.835 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST WYLAM | 20 | 66 | Coalburns | STELLA SOUTH | NE42 5EX | LTW (DFES) | 0.22636 | 0.10436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WESTERHOPE | 11 | 33 | Blucher | STELLA NORTH | NE5 5HH | LTW (DFES) | 19.0703 | 19.0043 | 18.9283 | 18.8393 | 18.7363 | 18.5673 | 18.3963 | 18.1913 | 17.9813 | 17.7653 | 16.6213 | 15.5633 | 14.5963 | 13.8183 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WESTOE | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 3GE | LTW (DFES) | 13.181 | 13.108 | 13.022 | 12.92 | 12.806 | 12.624 | 12.441 | 12.221 | 11.994 | 11.757 | 10.483 | 9.354 | 8.291 | 7.421 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO22 4JE | LTW (DFES) | 11.7941 | 11.7661 | 11.7401 | 11.7091 | 11.6751 | 11.6231 | 11.5701 | 11.5061 | 11.4391 | 11.3661 | 10.9621 | 10.6231 | 10.2871 | 10.0011 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO22 4JE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO21 1LY | LTW (DFES) | 11.7179 | 11.6859 | 11.6549 | 11.6189 | 11.5769 | 11.5129 | 11.4479 | 11.3679 | 11.2849 | 11.1969 | 10.7129 | 10.2899 | 9.8839 | 9.5409 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO21 1LY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WILLINGTON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 7HS | LTW (DFES) | 18.5602 | 18.4902 | 18.4072 | 18.3102 | 18.1992 | 18.0162 | 17.8322 | 17.6102 | 17.3832 | 17.1492 | 15.9112 | 14.7692 | 13.7232 | 12.8812 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | Wormald Green 132/11kV | KNARESBOROUGH | HG3 3PS | LTW (DFES) | 13.15 | 13.092 | 13.025 | 12.947 | 12.86 | 12.727 | 12.592 | 12.429 | 12.257 | 12.074 | 11.065 | 10.203 | 9.36 | 8.645 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WYNYARD | 11 | 66 | Hartmoor | HARTMOOR | TS2 2FB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | YEDINGHAM | 11 | 66 | Malton Grid | OSBALDWICK | YO17 8RR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | YORK UNIVERSITY | 11 | 33 | Melrosegate | OSBALDWICK | YO10 5ZF | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ABBEY ROAD | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS5 3NF | LTW (DFES) | 1.8583 | 1.8213 | 1.7753 | 1.7203 | 1.6573 | 1.5533 | 1.4463 | 1.3173 | 1.1853 | 1.0503 | 0.33133 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AIREDALE ROAD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 4LJ | LTW (DFES) | 13.0766 | 13.0496 | 13.0166 | 12.9766 | 12.9316 | 12.8546 | 12.7766 | 12.6816 | 12.5846 | 12.4856 | 11.9636 | 11.4496 | 10.9796 | 10.5956 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALDHAM | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S73 8SW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALFRED GELDER STREET | 11 | 33 | Hull South | CREYKE BECK | HU1 1EP | LTW (DFES) | 2.8759 | 2.8609 | 2.8429 | 2.8219 | 2.7979 | 2.7569 | 2.7149 | 2.6639 | 2.6129 | 2.5599 | 2.2859 | 2.0149 | 1.7689 | 1.5699 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T1 | 11 | 33 | Leeds East | SKELTON GRANGE | LS7 3QB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T2 | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 3QB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALVERTHORPE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 9PB | LTW (DFES) | 21.6713 | 21.6003 | 21.5023 | 21.3893 | 21.2623 | 21.0613 | 20.8573 | 20.6103 | 20.3543 | 20.0873 | 18.6443 | 17.3213 | 16.0593 | 14.9963 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARMOURIES DRIVE | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LT | LTW (DFES) | 7.111 | 7.094 | 7.072 | 7.046 | 7.017 | 6.968 | 6.918 | 6.858 | 6.796 | 6.733 | 6.397 | 6.071 | 5.771 | 5.524 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARMTHORPE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3DY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARUNDEL STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4PJ | LTW (DFES) | 4.4338 | 4.4248 | 4.4128 | 4.3998 | 4.3838 | 4.3578 | 4.3308 | 4.2988 | 4.2658 | 4.2328 | 4.0548 | 3.8798 | 3.7198 | 3.5898 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ASKERN | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN6 0BY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AUDBY LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 7SU | LTW (DFES) | 3.5504 | 3.4914 | 3.4034 | 3.3004 | 3.1894 | 3.0264 | 2.8594 | 2.6594 | 2.4454 | 2.2204 | 0.96138 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AUSTERFIELD | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN10 6HD | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BAILIFF BRIDGE | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 4DT | LTW (DFES) | 1.2995 | 1.2615 | 1.2155 | 1.1605 | 1.0985 | 0.99348 | 0.88448 | 0.75248 | 0.61648 | 0.47548 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BALBY | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN4 8DG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BALME STREET | 11 | 33 | Bradford | BRADFORD WEST | BD1 4BA | LTW (DFES) | 3.3186 | 3.2926 | 3.2596 | 3.2206 | 3.1756 | 3.0996 | 3.0216 | 2.9286 | 2.8326 | 2.7346 | 2.2186 | 1.7096 | 1.2456 | 0.8656 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNBURGH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 9NT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNOLDSWICK | 11 | 33 | Silsden | BRADFORD WEST | BB18 5RU | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 7AU | LTW (DFES) | 32.1582 | 32.1312 | 32.0992 | 32.0612 | 32.0172 | 31.9432 | 31.8672 | 31.7752 | 31.6822 | 31.5862 | 31.0812 | 30.5822 | 30.1282 | 29.7582 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARROW | 11 | 33 | Immingham | GRIMSBY WEST | DN19 7EG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 66/11KV | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1HT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARWICK | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS15 8SW | LTW (DFES) | 13.1074 | 13.0594 | 12.9974 | 12.9254 | 12.8434 | 12.7054 | 12.5644 | 12.3954 | 12.2214 | 12.0424 | 11.0964 | 10.1784 | 9.3324 | 8.6374 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BASLOW ROAD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S17 3LT | LTW (DFES) | 0.22592 | 0.18592 | 0.13592 | 0.077919 | 0.010919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BATLEY | 11 | 33 | Thornhill 132kV | ELLAND | WF17 6HU | LTW (DFES) | 4.8534 | 4.7874 | 4.7044 | 4.6064 | 4.4944 | 4.3064 | 4.1144 | 3.8834 | 3.6444 | 3.3994 | 2.1044 | 0.83742 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEAL | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8DT | LTW (DFES) | 3.9011 | 3.8671 | 3.8191 | 3.7621 | 3.7021 | 3.6111 | 3.5181 | 3.4031 | 3.2791 | 3.1471 | 2.4111 | 1.7611 | 1.1131 | 0.54107 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | LTW (DFES) | 8.5735 | 8.5585 | 8.5405 | 8.5185 | 8.4945 | 8.4525 | 8.4105 | 8.3605 | 8.3085 | 8.2545 | 7.9725 | 7.6975 | 7.4445 | 7.2375 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | LTW (DFES) | 38.4232 | 38.3892 | 38.3452 | 38.2942 | 38.2362 | 38.1382 | 38.0392 | 37.9192 | 37.7962 | 37.6692 | 37.0002 | 36.3502 | 35.7512 | 35.2592 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEIGHTON | 11 | 66 | Thurcroft | THURCROFT | S26 4TL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELLHOUSE ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 0PL | LTW (DFES) | 1.3237 | 1.2597 | 1.1797 | 1.0867 | 0.97873 | 0.79473 | 0.60773 | 0.38173 | 0.15073 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT AVENUE | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DF | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT COVERT | 11 | 33 | Wold Newton | KEADBY | LN11 9RA | LTW (DFES) | 0.020462 | 0.013462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELTHORPE LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1SB | LTW (DFES) | 12.335 | 12.324 | 12.307 | 12.287 | 12.267 | 12.237 | 12.206 | 12.167 | 12.125 | 12.08 | 11.826 | 11.607 | 11.384 | 11.183 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BENTLEY | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN5 0NG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BILLET LANE | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINBROOK | 11 | 33 | Wold Newton | KEADBY | LN8 6DR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 33/11KV | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | LTW (DFES) | 13.4026 | 13.3536 | 13.2926 | 13.2206 | 13.1376 | 12.9986 | 12.8576 | 12.6856 | 12.5106 | 12.3306 | 11.3806 | 10.4466 | 9.5936 | 8.8936 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BIRKBY | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 5HB | LTW (DFES) | 0.27855 | 0.22755 | 0.16355 | 0.088548 | 0.0025485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1HF | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLUE BOY STREET | 11 | 33 | Neepsend | NEEPSEND | S3 7BA | LTW (DFES) | 1.359 | 1.349 | 1.337 | 1.322 | 1.305 | 1.277 | 1.248 | 1.213 | 1.177 | 1.14 | 0.94596 | 0.75396 | 0.57996 | 0.43696 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOC BRINSWORTH | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1WT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOLTON ROAD | 11 | 33 | Silsden | BRADFORD WEST | BD20 0JT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOTTESFORD | 11 | 33 | Scunthorpe South | KEADBY | DN16 3UJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHOPE | 11 | 33 | Menston | BRADFORD WEST | LS16 9HA | LTW (DFES) | 0.75111 | 0.73911 | 0.72411 | 0.70611 | 0.68511 | 0.65111 | 0.61611 | 0.57411 | 0.53111 | 0.48611 | 0.25111 | 0.02311 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMLEY | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS13 3ST | LTW (DFES) | 21.6288 | 21.5618 | 21.4768 | 21.3768 | 21.2628 | 21.0728 | 20.8788 | 20.6448 | 20.4038 | 20.1568 | 18.8498 | 17.5808 | 16.4118 | 15.4508 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRETT STREET | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 4HW | LTW (DFES) | 17.1275 | 16.9895 | 16.7905 | 16.5615 | 16.3175 | 15.9495 | 15.5675 | 15.0975 | 14.5875 | 14.0415 | 10.9785 | 8.2605 | 5.5415 | 3.1205 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIDGES ROAD | 11 | 33 | Scunthorpe South | KEADBY | DN17 1HA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1QE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRODSWORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 7XB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BROOKFIELD STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LD | LTW (DFES) | 2.5359 | 2.5349 | 2.5319 | 2.5299 | 2.5269 | 2.5219 | 2.5169 | 2.5099 | 2.5039 | 2.4979 | 2.4629 | 2.4289 | 2.3979 | 2.3729 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BTP | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN31 2RL | LTW (DFES) | 16.3847 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3827 | 16.3817 | 16.3807 | 16.3797 | 16.3787 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURLEY STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS3 1JY | LTW (DFES) | 39.9951 | 39.9761 | 39.9521 | 39.9231 | 39.8911 | 39.8361 | 39.7801 | 39.7131 | 39.6441 | 39.5731 | 39.1981 | 38.8341 | 38.4981 | 38.2231 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURMANTOFTS | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 7SS | LTW (DFES) | 10.3155 | 10.3005 | 10.2805 | 10.2585 | 10.2325 | 10.1885 | 10.1445 | 10.0915 | 10.0365 | 9.9805 | 9.6835 | 9.3955 | 9.1295 | 8.9115 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURNLEYVILLE | 11 | 33 | Heckmondwike | SKELTON GRANGE | BD19 4RY | LTW (DFES) | 1.8754 | 1.8234 | 1.7584 | 1.6824 | 1.5954 | 1.4484 | 1.2984 | 1.1174 | 0.9304 | 0.7394 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURTON PIDSEA | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU12 9AE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURTON ROAD | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 2QG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 2HG | LTW (DFES) | 10.8123 | 10.7653 | 10.7053 | 10.6343 | 10.5533 | 10.4193 | 10.2813 | 10.1153 | 9.9453 | 9.7703 | 8.8443 | 7.9463 | 7.1183 | 6.4383 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BUTTERWICK | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO17 8HF | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CAISTOR | 11 | 33 | Wold Newton | KEADBY | LN7 6RE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CALDER WHARF | 11 | 33 | Thornhill 132kV | ELLAND | WF13 3JQ | LTW (DFES) | 19.9048 | 19.8488 | 19.7778 | 19.6948 | 19.6008 | 19.4418 | 19.2808 | 19.0848 | 18.8838 | 18.6778 | 17.5828 | 16.5158 | 15.5338 | 14.7238 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CARLTON HILL | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 1JB | LTW (DFES) | 22.2124 | 22.1914 | 22.1644 | 22.1334 | 22.0984 | 22.0384 | 21.9784 | 21.9054 | 21.8304 | 21.7534 | 21.3474 | 20.9524 | 20.5884 | 20.2894 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CARR LANE | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 4PS | LTW (DFES) | 22.4557 | 22.4077 | 22.3437 | 22.2677 | 22.1827 | 22.0497 | 21.9137 | 21.7497 | 21.5787 | 21.4017 | 20.4417 | 19.5617 | 18.7217 | 18.0147 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CHELKER RESERVOIR | 11 | 33 | Silsden | BRADFORD WEST | LS29 0JS | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CHEVIN END | 11 | 33 | Menston | BRADFORD WEST | LS29 6BE | LTW (DFES) | 23.4135 | 23.3815 | 23.3405 | 23.2935 | 23.2395 | 23.1475 | 23.0535 | 22.9405 | 22.8245 | 22.7055 | 22.0785 | 21.4635 | 20.9005 | 20.4395 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENCE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1JE | LTW (DFES) | 7.635 | 7.623 | 7.608 | 7.591 | 7.571 | 7.537 | 7.503 | 7.462 | 7.42 | 7.377 | 7.147 | 6.925 | 6.72 | 6.552 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON ROAD | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS2 9JT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON STREET | 11 | 33 | Hull South | CREYKE BECK | HU3 1AP | LTW (DFES) | 22.2799 | 22.2529 | 22.2209 | 22.1819 | 22.1379 | 22.0619 | 21.9839 | 21.8919 | 21.7969 | 21.7009 | 21.1979 | 20.6999 | 20.2499 | 19.8859 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLAYWHEELS LANE | 11 | 33 | Neepsend | NEEPSEND | S6 1LY | LTW (DFES) | 22.6381 | 22.5541 | 22.4491 | 22.3261 | 22.1851 | 21.9441 | 21.6981 | 21.4021 | 21.0991 | 20.7891 | 19.1581 | 17.5461 | 16.0781 | 14.8791 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLOUGH LANE | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3EH | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COMMONSIDE LANE | 11 | 33 | Featherstone | FERRYBRIDGE B | WF7 5DF | LTW (DFES) | 5.3548 | 5.3128 | 5.2548 | 5.8868 | 5.8108 | 5.6918 | 5.5698 | 5.4228 | 5.2708 | 5.1118 | 4.2518 | 3.4648 | 2.7128 | 2.0798 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CONVAMORE ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN32 9PG | LTW (DFES) | 14.0593 | 14.0123 | 13.9493 | 13.8753 | 13.7923 | 13.6593 | 13.5243 | 13.3603 | 13.1913 | 13.0153 | 12.0683 | 11.1873 | 10.3533 | 9.6543 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CONYARD ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN35 7LQ | LTW (DFES) | 10.7296 | 10.6666 | 10.5826 | 10.4846 | 10.3746 | 10.1976 | 10.0166 | 9.7996 | 9.5736 | 9.3396 | 8.0776 | 6.9036 | 5.7926 | 4.8616 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CORNWALL STREET | 11 | 132 | Cornwall Street | CREYKE BECK | HU8 8AQ | LTW (DFES) | 32.4377 | 32.4117 | 32.3807 | 32.3427 | 32.2997 | 32.2267 | 32.1517 | 32.0617 | 31.9707 | 31.8777 | 31.3917 | 30.9107 | 30.4757 | 30.1237 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CORRINGHAM ROAD | 11 | 33 | Blyton | KEADBY | DN21 1FT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COSTHORPE | 11 | 66 | Thurcroft | THURCROFT | S81 9QR | LTW (DFES) | 6.6581 | 6.6291 | 6.5811 | 6.5261 | 6.4681 | 6.3901 | 6.3111 | 6.2141 | 6.1071 | 5.9911 | 5.3221 | 4.7971 | 4.2351 | 3.7241 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COUNTY ROAD NORTH | 11 | 33 | Hull South | CREYKE BECK | HU5 5DR | LTW (DFES) | 8.2864 | 8.1854 | 8.0514 | 7.8964 | 7.7214 | 7.4374 | 7.1454 | 6.7924 | 6.4254 | 6.0434 | 3.9904 | 2.0444 | 0.2134 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CRACOE | 11 | 33 | Silsden | BRADFORD WEST | BD23 6BE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROOKESMOOR ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 3FP | LTW (DFES) | 3.5737 | 3.5057 | 3.4217 | 3.3227 | 3.2097 | 3.0167 | 2.8197 | 2.5817 | 2.3387 | 2.0897 | 0.78171 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROSSHILLS | 11 | 33 | Silsden | BRADFORD WEST | BD20 7AQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROWLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN17 4BB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROWN STREET | 11 | 33 | Girlington | BRADFORD WEST | BD1 2LA | LTW (DFES) | 0.78271 | 0.77471 | 0.76571 | 0.75471 | 0.74271 | 0.72171 | 0.69971 | 0.67471 | 0.64771 | 0.62071 | 0.47771 | 0.33671 | 0.20871 | 0.10371 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DALTON | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD2 1FF | LTW (DFES) | 2.704 | 2.629 | 2.535 | 2.424 | 2.298 | 2.085 | 1.868 | 1.606 | 1.337 | 1.06 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DARNALL | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 4JT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DEARNE ROAD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DEIGHTON | 11 | 33 | Brighouse 132/33kV | ELLAND | HD2 1UP | LTW (DFES) | 18.449 | 18.406 | 18.353 | 18.289 | 18.217 | 18.095 | 17.971 | 17.821 | 17.667 | 17.509 | 16.671 | 15.851 | 15.098 | 14.478 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENBY DALE ROAD | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7BH | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENBY GRANGE | 11 | 33 | Thornhill 132kV | ELLAND | WF4 4JG | LTW (DFES) | 0.32111 | 0.30611 | 0.28511 | 0.26111 | 0.23511 | 0.19111 | 0.14711 | 0.09411 | 0.03911 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENHOLME | 11 | 33 | Holmfield | BRADFORD WEST | BD13 4JF | LTW (DFES) | 11.6027 | 11.5867 | 11.5677 | 11.5457 | 11.5197 | 11.4767 | 11.4317 | 11.3787 | 11.3237 | 11.2677 | 10.9707 | 10.6797 | 10.4127 | 10.1947 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DINNINGTON | 11 | 66 | Thurcroft | THURCROFT | S25 3QT | LTW (DFES) | 0 | 22.4087 | 22.3237 | 22.2247 | 22.1147 | 21.9377 | 21.7577 | 21.5407 | 21.3157 | 21.0817 | 19.8157 | 18.6447 | 17.5327 | 16.5977 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DOUGHTY ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN32 0LR | LTW (DFES) | 3.8848 | 3.7958 | 3.6778 | 3.5388 | 3.3828 | 3.1328 | 2.8788 | 2.5718 | 2.2528 | 1.9218 | 0.1418 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DOWKER STREET | 11 | 33 | Lindley | ELLAND | HD3 4JB | LTW (DFES) | 0.51651 | 0.47751 | 0.42751 | 0.36951 | 0.30351 | 0.19151 | 0.077515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRAX PRIMARY | 11 | 66 | Camblesforth | CAMBLESFORTH | YO8 6PQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 5XR | LTW (DFES) | 13.8755 | 13.7395 | 13.5425 | 13.3175 | 13.0755 | 12.7125 | 12.3355 | 11.8715 | 11.3685 | 10.8285 | 7.8045 | 5.1215 | 2.4375 | 0.047461 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRONFIELD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S18 2XU | LTW (DFES) | 1.6952 | 1.6642 | 1.6242 | 1.5782 | 1.5252 | 1.4392 | 1.3502 | 1.2432 | 1.1312 | 1.0142 | 0.3892 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DUDLEY HILL | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9NW | LTW (DFES) | 23.1648 | 23.1348 | 23.0968 | 23.0528 | 23.0018 | 22.9148 | 22.8268 | 22.7198 | 22.6108 | 22.4998 | 21.9108 | 21.3318 | 20.8028 | 20.3698 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DUNKESWICK | 11 | 33 | Bramham | FERRYBRIDGE B | LS17 9LP | LTW (DFES) | 12.0353 | 11.9863 | 11.8913 | 11.7853 | 11.6763 | 11.5433 | 11.4083 | 11.2453 | 11.0623 | 10.8603 | 9.6473 | 8.8083 | 7.8383 | 6.9273 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DURKAR LOW LANE | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF4 3BJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EASINGTON | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0SU | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EASTFIELD ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ECCLESFIELD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 9YR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EDLINGTON | 11 | 66 | Thurcroft | THURCROFT | DN12 1SU | LTW (DFES) | 13.5945 | 13.5195 | 13.4185 | 13.3015 | 13.1705 | 12.9615 | 12.7475 | 12.4885 | 12.2185 | 11.9355 | 10.4065 | 8.9845 | 7.6315 | 6.4835 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EGGBOROUGH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | DN14 0QA | LTW (DFES) | 7.4326 | 7.4176 | 7.3946 | 7.3676 | 7.3396 | 7.2986 | 7.2556 | 7.2026 | 7.1456 | 7.0836 | 6.7346 | 6.4306 | 6.1236 | 5.8476 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELGAR ROAD | 11 | 33 | Hull West | CREYKE BECK | HU4 7NY | LTW (DFES) | 21.9877 | 21.8787 | 21.7267 | 21.5507 | 21.3587 | 21.0617 | 20.7547 | 20.3797 | 19.9787 | 19.5537 | 17.2087 | 15.0767 | 12.9917 | 11.1707 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLAND 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX5 9AE | LTW (DFES) | 19.9975 | 19.9605 | 19.9145 | 19.8615 | 19.8005 | 19.6965 | 19.5895 | 19.4595 | 19.3255 | 19.1875 | 18.4555 | 17.7275 | 17.0605 | 16.5065 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIFOOT LANE | 11 | 33 | Saltend 132/33kV | SALTEND NORTH | HU12 9EB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 1/3 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | LTW (DFES) | 4.8098 | 4.7828 | 4.7498 | 4.7108 | 4.6648 | 4.5878 | 4.5098 | 4.4148 | 4.3178 | 4.2188 | 3.6968 | 3.1808 | 2.7118 | 2.3278 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 2 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 1 | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 4LS | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 2 | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S75 4LS | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELSECAR | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S74 8AU | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ENDIKE LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 8AY | LTW (DFES) | 16.5354 | 16.4714 | 16.3864 | 16.2874 | 16.1774 | 16.0004 | 15.8184 | 15.5974 | 15.3654 | 15.1244 | 13.8204 | 12.5954 | 11.4324 | 10.4464 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EPWORTH | 11 | 33 | Blyton | KEADBY | DN9 1JU | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FARNLEY CRESCENT | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 5AN | LTW (DFES) | 0.85508 | 0.80108 | 0.73408 | 0.65408 | 0.56408 | 0.41208 | 0.25808 | 0.072077 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FENTON LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6EZ | LTW (DFES) | 5.1002 | 5.0762 | 5.0412 | 5.0012 | 4.9592 | 4.8962 | 4.8312 | 4.7512 | 4.6642 | 4.5702 | 4.0422 | 3.5812 | 3.1152 | 2.6982 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF11 8RR | LTW (DFES) | 2.182 | 2.073 | 1.921 | 1.744 | 1.549 | 1.246 | 0.936 | 0.56 | 0.164 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIR TREE LANE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS17 7BZ | LTW (DFES) | 3.8808 | 3.8138 | 3.7288 | 3.6288 | 3.5148 | 3.3238 | 3.1298 | 2.8948 | 2.6538 | 2.4068 | 1.0968 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIRST AVENUE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 9NE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIRTH BROWN | 11 | 33 | Santon | KEADBY | DN16 1XP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FISH DAM LANE | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 3HQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FLIXBOROUGH | 11 | 33 | Scunthorpe North | KEADBY | DN15 8RR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOLLY HALL | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 3TF | LTW (DFES) | 1.8137 | 1.7817 | 1.7417 | 1.6947 | 1.6407 | 1.5497 | 1.4577 | 1.3457 | 1.2307 | 1.1127 | 0.4877 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOUR LANE ENDS | 11 | 33 | Girlington | BRADFORD WEST | BD8 0LJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOXHILLS | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FULLERTON ROAD | 11 | 33 | Templeborough 275/33KV | TEMPLEBOROUGH 275/33KV | S60 1DL | LTW (DFES) | 0.11387 | 0.08887 | 0.05487 | 0.01587 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FURNESS AVENUE | 11 | 33 | Holmfield | BRADFORD WEST | WF8 3JA | LTW (DFES) | 1.1489 | 1.0909 | 1.0209 | 0.93786 | 0.84286 | 0.68186 | 0.51486 | 0.31386 | 0.10486 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GAISBY LANE | 11 | 33 | Bradford | BRADFORD WEST | BD2 1BB | LTW (DFES) | 3.141 | 3.086 | 3.018 | 2.938 | 2.847 | 2.691 | 2.532 | 2.341 | 2.145 | 1.944 | 0.88698 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIBRALTAR ROAD | 11 | 33 | Holmfield | BRADFORD WEST | HX1 4HL | LTW (DFES) | 4.3461 | 4.2661 | 4.1691 | 4.0541 | 3.9241 | 3.7011 | 3.4721 | 3.1941 | 2.9061 | 2.6091 | 1.0371 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIBSON LANE | 11 | 33 | Hull West | CREYKE BECK | HU14 3HH | LTW (DFES) | 17.086 | 16.984 | 16.836 | 16.666 | 16.483 | 16.21 | 15.926 | 15.577 | 15.197 | 14.791 | 12.513 | 10.491 | 8.47 | 6.669 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GILDERSOME | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 7HW | LTW (DFES) | 0.66287 | 0.63287 | 0.59487 | 0.54887 | 0.49787 | 0.41087 | 0.32287 | 0.21687 | 0.10787 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GLEADLESS VALLEY | 11 | 33 | Norton Lees | NORTON LEES | S14 1FP | LTW (DFES) | 1.785 | 1.728 | 1.659 | 1.577 | 1.483 | 1.323 | 1.16 | 0.96298 | 0.76098 | 0.55498 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GOOLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 6SX | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GRAINTHORPE | 11 | 33 | Wold Newton | KEADBY | LN11 7JU | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREAT COATES | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN37 9PN | LTW (DFES) | 2.1801 | 2.1101 | 2.0141 | 1.9021 | 1.7771 | 1.5801 | 1.3791 | 1.1371 | 0.88409 | 0.62109 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREENHILL | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 7RJ | LTW (DFES) | 0.87623 | 0.84223 | 0.80123 | 0.75123 | 0.69523 | 0.59923 | 0.50223 | 0.38423 | 0.26323 | 0.13923 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS RD | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GRIMETHORPE | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S72 7BQ | LTW (DFES) | 15.5529 | 15.5199 | 15.4769 | 15.4249 | 15.3679 | 15.2769 | 15.1839 | 15.0709 | 14.9539 | 14.8309 | 14.1699 | 13.5569 | 12.9729 | 12.4809 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GROVE STREET | 11 | 33 | Lindley | ELLAND | HD1 2PB | LTW (DFES) | 13.6802 | 13.6692 | 13.6552 | 13.6392 | 13.6212 | 13.5902 | 13.5592 | 13.5212 | 13.4822 | 13.4422 | 13.2302 | 13.0222 | 12.8312 | 12.6742 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GUARDIAN GLASS | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8GA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HACKENTHORPE | 11 | 66 | Thurcroft | THURCROFT | S12 4ET | LTW (DFES) | 24.2326 | 24.1746 | 24.1046 | 24.0216 | 23.9266 | 23.7636 | 23.5986 | 23.3986 | 23.1946 | 22.9856 | 21.8856 | 20.7986 | 19.8086 | 19.0006 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 33/11KV | 11 | 33 | Halifax 132/33kV | ELLAND | HX1 1XB | LTW (DFES) | 2.4206 | 2.3686 | 2.3046 | 2.2296 | 2.1436 | 1.9966 | 1.8466 | 1.6636 | 1.4746 | 1.2786 | 0.24562 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALLAM STREET | 11 | 33 | Menston | BRADFORD WEST | LS20 8AG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARDEN | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 1BG | LTW (DFES) | 6.1403 | 6.1233 | 6.1033 | 6.0793 | 6.0523 | 6.0053 | 5.9583 | 5.9003 | 5.8423 | 5.7823 | 5.4653 | 5.1533 | 4.8683 | 4.6363 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARPSWELL | 11 | 33 | Blyton | KEADBY | DN21 5UT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARWORTH | 11 | 66 | Thurcroft | THURCROFT | DN11 8JW | LTW (DFES) | 19.5745 | 19.5415 | 19.4895 | 19.4315 | 19.3675 | 19.2765 | 19.1835 | 19.0695 | 18.9475 | 18.8175 | 18.0825 | 17.4635 | 16.8345 | 16.2765 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 1 | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD22 9EP | LTW (DFES) | 13.6766 | 13.6516 | 13.6206 | 13.5836 | 13.5416 | 13.4706 | 13.3986 | 13.3106 | 13.2206 | 13.1296 | 12.6456 | 12.1696 | 11.7346 | 11.3786 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 2 | 11 | 33 | Silsden | BRADFORD WEST | BD22 9EP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAXEY | 11 | 33 | Blyton | KEADBY | DN9 2LT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAYTON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1RJ | LTW (DFES) | 0 | 0 | 0 | 16.1935 | 16.0605 | 15.8625 | 15.6555 | 15.4015 | 15.1265 | 14.8305 | 13.1745 | 11.7055 | 10.2355 | 8.9265 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAZLEHEAD | 11 | 33 | Thornhill 132kV | ELLAND | S36 4HG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEBDEN BRIDGE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 6LX | LTW (DFES) | 7.4947 | 7.4787 | 7.4597 | 7.4367 | 7.4097 | 7.3657 | 7.3187 | 7.2637 | 7.2057 | 7.1457 | 6.8297 | 6.5147 | 6.2267 | 5.9867 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEDLEY CHASE | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 1YN | LTW (DFES) | 12.6968 | 12.6838 | 12.6678 | 12.6488 | 12.6268 | 12.5898 | 12.5528 | 12.5078 | 12.4618 | 12.4148 | 12.1648 | 11.9218 | 11.6988 | 11.5148 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEDON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 8ED | LTW (DFES) | 11.4115 | 11.4075 | 11.4025 | 11.3965 | 11.3905 | 11.3785 | 11.3675 | 11.3535 | 11.3395 | 11.3255 | 11.2505 | 11.1765 | 11.1105 | 11.0565 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEMSWORTH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 5BZ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 1 | 11 | 33 | Hull South | CREYKE BECK | HU4 6SP | LTW (DFES) | 0.86984 | 0.84384 | 0.80684 | 0.76584 | 0.71984 | 0.64884 | 0.57584 | 0.48584 | 0.39084 | 0.28984 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 2 | 11 | 33 | Hull West | CREYKE BECK | HU4 6SP | LTW (DFES) | 1.4945 | 1.4705 | 1.4365 | 1.3975 | 1.3545 | 1.2865 | 1.2175 | 1.1325 | 1.0425 | 0.94752 | 0.42652 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HIBALDSTOW | 11 | 33 | Santon | KEADBY | DN21 4NH | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HICKLETON | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 0DE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HILLCREST | 11 | 33 | Leeds East | SKELTON GRANGE | LS8 3AA | LTW (DFES) | 3.5189 | 3.4539 | 3.3729 | 3.2769 | 3.1679 | 2.9849 | 2.7989 | 2.5749 | 2.3439 | 2.1079 | 0.85393 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLBECK | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9SZ | LTW (DFES) | 4.061 | 4.012 | 3.95 | 3.877 | 3.793 | 3.654 | 3.511 | 3.339 | 3.163 | 2.982 | 2.023 | 1.092 | 0.23502 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLDERNESS | 11 | 33 | Bransholme | CREYKE BECK | HU9 4AU | LTW (DFES) | 0.14351 | 0.054508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 4BX | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 20.5125 | 20.4275 | 20.3235 | 20.2115 | 20.0895 | 19.4095 | 18.8105 | 18.2085 | 17.6715 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HONLEY | 11 | 33 | Lindley | ELLAND | HD9 6RU | LTW (DFES) | 10.4279 | 10.3749 | 10.3099 | 10.2319 | 10.1439 | 9.9959 | 9.8439 | 9.6619 | 9.4739 | 9.2799 | 8.2579 | 7.2589 | 6.3399 | 5.5839 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOPE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S33 6RP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HORBURY | 11 | 33 | Thornhill 132kV | ELLAND | WF4 6EU | LTW (DFES) | 17.9703 | 17.9133 | 17.8343 | 17.7433 | 17.6413 | 17.4793 | 17.3153 | 17.1173 | 16.9103 | 16.6963 | 15.5363 | 14.4713 | 13.4563 | 12.6013 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOUGHTON MAIN | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S72 0GX | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 33/11KV | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5NP | LTW (DFES) | 22.7376 | 22.6556 | 22.5396 | 22.4056 | 22.2606 | 22.0406 | 21.8126 | 21.5326 | 21.2306 | 20.9086 | 19.1176 | 17.5106 | 15.9196 | 14.5146 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUMBER ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LZ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNMANBY | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO14 0JY | LTW (DFES) | 20.2215 | 20.1485 | 20.0135 | 19.8605 | 19.7045 | 19.5115 | 19.3135 | 19.0715 | 18.7985 | 18.4975 | 16.6925 | 15.3925 | 13.9165 | 12.5255 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ICI FIBRES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4LT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IDLE | 11 | 33 | Bradford | BRADFORD WEST | BD10 8SA | LTW (DFES) | 2.6571 | 2.5981 | 2.5241 | 2.4381 | 2.3381 | 2.1701 | 1.9981 | 1.7911 | 1.5781 | 1.3611 | 0.21505 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ILKLEY | 11 | 33 | Silsden | BRADFORD WEST | LS29 9BE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | INGS LANE | 11 | 33 | Silsden | BRADFORD WEST | BD23 1UP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IVESON HOUSE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 6RF | LTW (DFES) | 20.8886 | 20.8286 | 20.7516 | 20.6616 | 20.5586 | 20.3866 | 20.2106 | 19.9996 | 19.7816 | 19.5586 | 18.3776 | 17.2306 | 16.1746 | 15.3056 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | JARRATT STREET | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN1 2BS | LTW (DFES) | 13.1068 | 13.0668 | 13.0128 | 12.9498 | 12.8798 | 12.7678 | 12.6528 | 12.5148 | 12.3698 | 12.2178 | 11.3988 | 10.6378 | 9.9128 | 9.2978 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KEDDINGTON ROAD | 11 | 33 | Wold Newton | KEADBY | LN11 0DE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KEIGHLEY | 11 | 132 | Keighley | BRADFORD WEST | BD21 5AJ | LTW (DFES) | 30.4249 | 30.3919 | 30.3509 | 30.3019 | 30.2459 | 30.1509 | 30.0549 | 29.9379 | 29.8189 | 29.6969 | 29.0529 | 28.4189 | 27.8399 | 27.3659 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KENMORE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 0XE | LTW (DFES) | 18.8849 | 18.8589 | 18.8229 | 18.7819 | 18.7349 | 18.6609 | 18.5869 | 18.4959 | 18.4019 | 18.3049 | 17.7759 | 17.2919 | 16.8289 | 16.4399 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KILLINGHALL ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD3 8HN | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KILNHURST | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S64 5TL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KING GEORGE DOCK | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5PL | LTW (DFES) | 23.859 | 23.856 | 23.853 | 23.848 | 23.843 | 23.835 | 23.826 | 23.815 | 23.805 | 23.794 | 23.737 | 23.681 | 23.63 | 23.589 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRK DRIVE | 11 | 33 | Menston | BRADFORD WEST | BD17 6SA | LTW (DFES) | 1.0634 | 1.0224 | 0.97238 | 0.91338 | 0.84438 | 0.72938 | 0.61138 | 0.46938 | 0.32338 | 0.17438 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRK SANDALL | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 1QP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKBURN | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 9EH | LTW (DFES) | 6.1532 | 6.1222 | 6.0742 | 6.0192 | 5.9612 | 5.8782 | 5.7932 | 5.6882 | 5.5732 | 5.4492 | 4.7402 | 4.1452 | 3.5302 | 2.9742 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIVETON PARK | 11 | 66 | Thurcroft | THURCROFT | S26 6RP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KNOSTROP | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0PJ | LTW (DFES) | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEA ROAD | 11 | 33 | Blyton | KEADBY | DN21 1ND | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEASOWE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 2EY | LTW (DFES) | 6.848 | 6.816 | 6.775 | 6.726 | 6.671 | 6.579 | 6.486 | 6.373 | 6.257 | 6.137 | 5.506 | 4.893 | 4.329 | 3.865 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEDSTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF10 2AX | LTW (DFES) | 1.3188 | 1.2708 | 1.2088 | 1.1368 | 1.0548 | 0.9188 | 0.7798 | 0.6118 | 0.4388 | 0.2618 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS ROAD | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 5AA | LTW (DFES) | 0.39149 | 0.37049 | 0.34449 | 0.31449 | 0.27949 | 0.22049 | 0.16049 | 0.088491 | 0.014491 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEGRAMS MILL LANE | 11 | 33 | Girlington | BRADFORD WEST | BD7 2BA | LTW (DFES) | 21.2458 | 21.2108 | 21.1688 | 21.1188 | 21.0618 | 20.9648 | 20.8658 | 20.7468 | 20.6248 | 20.4998 | 19.8398 | 19.1908 | 18.5978 | 18.1128 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEYLANDS ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS2 7QB | LTW (DFES) | 16.1512 | 16.1422 | 16.1302 | 16.1162 | 16.0992 | 16.0722 | 16.0452 | 16.0122 | 15.9782 | 15.9432 | 15.7582 | 15.5782 | 15.4132 | 15.2772 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LIVERSEDGE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF15 7NY | LTW (DFES) | 1.7819 | 1.7449 | 1.6999 | 1.6459 | 1.5839 | 1.4799 | 1.3739 | 1.2459 | 1.1149 | 0.97988 | 0.26488 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOUTH | 11 | 33 | Wold Newton | KEADBY | LN11 0WA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOW MOOR | 11 | 33 | Staygate | SKELTON GRANGE | BD12 0NG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOWFIELDS | 11 | 33 | Brighouse 132/33kV | ELLAND | HX5 9DE | LTW (DFES) | 25.258 | 25.256 | 25.255 | 25.253 | 25.251 | 25.247 | 25.244 | 25.239 | 25.235 | 25.23 | 25.205 | 25.18 | 25.158 | 25.139 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOXLEY ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 6SJ | LTW (DFES) | 0.24826 | 0.24526 | 0.24126 | 0.23626 | 0.23126 | 0.22226 | 0.21226 | 0.20126 | 0.18926 | 0.17726 | 0.11426 | 0.051257 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANCHESTER ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD5 0QL | LTW (DFES) | 3.0867 | 3.0757 | 3.0637 | 3.0487 | 3.0307 | 3.0017 | 2.9717 | 2.9357 | 2.8987 | 2.8617 | 2.6627 | 2.4667 | 2.2877 | 2.1407 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 1 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S12 2DL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 2 | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S12 2DL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARKHAM GATES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 2FS | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARMION ROAD | 11 | 33 | Norton Lees | NORTON LEES | S11 8TS | LTW (DFES) | 2.6478 | 2.5738 | 2.4828 | 2.3758 | 2.2518 | 2.0428 | 1.8278 | 1.5698 | 1.3058 | 1.0358 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARSDEN ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN31 3SQ | LTW (DFES) | 5.0209 | 4.9869 | 4.9399 | 4.8859 | 4.8249 | 4.7279 | 4.6279 | 4.5079 | 4.3839 | 4.2549 | 3.5589 | 2.9109 | 2.2989 | 1.7849 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARTONGATE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 6RX | LTW (DFES) | 0 | 0 | 0 | 19.1225 | 18.8905 | 18.5425 | 18.1805 | 17.7355 | 17.2525 | 16.7345 | 13.8345 | 11.2605 | 8.6865 | 6.3935 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MELTHAM | 11 | 33 | Lindley | ELLAND | HD9 4AL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MEXBOROUGH 1_2 | 11 | 66 | Thurcroft | THURCROFT | S64 0JD | LTW (DFES) | 24.654 | 24.549 | 24.408 | 24.244 | 24.061 | 23.769 | 23.47 | 23.108 | 22.729 | 22.334 | 20.195 | 18.208 | 16.316 | 14.712 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MIDDLETON TOWN STREET | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS10 3TQ | LTW (DFES) | 16.399 | 16.346 | 16.278 | 16.199 | 16.108 | 15.956 | 15.801 | 15.615 | 15.423 | 15.227 | 14.185 | 13.173 | 12.242 | 11.477 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILLHOUSES | 11 | 33 | Jordanthorpe | JORDANTHORPE | S7 2QH | LTW (DFES) | 1.2795 | 1.2525 | 1.2195 | 1.1805 | 1.1355 | 1.0585 | 0.98052 | 0.88652 | 0.79052 | 0.69152 | 0.17252 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILLROYD STREET | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1JZ | LTW (DFES) | 14.3257 | 14.2727 | 14.2087 | 14.1327 | 14.0457 | 13.8987 | 13.7467 | 13.5627 | 13.3727 | 13.1757 | 12.1367 | 11.1027 | 10.1547 | 9.3677 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILTON PLACE | 11 | 33 | Wakefield North | SKELTON GRANGE | WF5 9EG | LTW (DFES) | 18.6867 | 18.6167 | 18.5227 | 18.4117 | 18.2877 | 18.0897 | 17.8887 | 17.6457 | 17.3937 | 17.1317 | 15.7187 | 14.4117 | 13.1717 | 12.1297 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MIRFIELD | 11 | 33 | Thornhill 132kV | ELLAND | WF14 8NF | LTW (DFES) | 19.582 | 19.516 | 19.434 | 19.337 | 19.226 | 19.04 | 18.85 | 18.621 | 18.385 | 18.143 | 16.859 | 15.606 | 14.453 | 13.504 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MONCKTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S71 4BG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOOR ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS6 4BJ | LTW (DFES) | 23.2606 | 23.1916 | 23.1036 | 22.9996 | 22.8816 | 22.6846 | 22.4826 | 22.2406 | 21.9906 | 21.7356 | 20.3796 | 19.0636 | 17.8526 | 16.8566 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOORSIDE ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD2 3RJ | LTW (DFES) | 20.2239 | 20.1609 | 20.0839 | 19.9939 | 19.8889 | 19.7119 | 19.5319 | 19.3139 | 19.0919 | 18.8629 | 17.6609 | 16.4759 | 15.3949 | 14.5099 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MORLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 9HS | LTW (DFES) | 19.8637 | 19.8107 | 19.7447 | 19.6667 | 19.5767 | 19.4277 | 19.2757 | 19.0927 | 18.9047 | 18.7117 | 17.6877 | 16.6947 | 15.7797 | 15.0277 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOUNT STREET | 11 | 33 | Bradford | BRADFORD WEST | BD4 8TB | LTW (DFES) | 21.018 | 21.003 | 20.984 | 20.963 | 20.938 | 20.896 | 20.853 | 20.801 | 20.748 | 20.694 | 20.407 | 20.125 | 19.867 | 19.657 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MYTHOLMROYD | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 8NE | LTW (DFES) | 13.7861 | 13.7571 | 13.7211 | 13.6791 | 13.6311 | 13.5501 | 13.4661 | 13.3641 | 13.2581 | 13.1491 | 12.5741 | 12.0001 | 11.4741 | 11.0381 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NAB LANE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 9NE | LTW (DFES) | 12.0106 | 11.9776 | 11.9366 | 11.8886 | 11.8326 | 11.7396 | 11.6446 | 11.5296 | 11.4116 | 11.2906 | 10.6486 | 10.0206 | 9.4446 | 8.9696 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NABWOOD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD18 4AA | LTW (DFES) | 13.4441 | 13.3961 | 13.3371 | 13.2661 | 13.1861 | 13.0491 | 12.9101 | 12.7421 | 12.5701 | 12.3941 | 11.4661 | 10.5521 | 9.7181 | 9.0351 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NATIONAL AVENUE | 11 | 33 | Hull South | CREYKE BECK | HU5 4JN | LTW (DFES) | 0.79437 | 0.76637 | 0.73137 | 0.69037 | 0.64237 | 0.56137 | 0.47837 | 0.37937 | 0.27837 | 0.17637 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | Wincobank | WINCOBANK | S61 2DL | LTW (DFES) | 18.9652 | 18.9162 | 18.8502 | 18.7732 | 18.6862 | 18.5492 | 18.4092 | 18.2392 | 18.0632 | 17.8812 | 16.8922 | 15.9802 | 15.1122 | 14.3822 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEW ORCHARD LANE | 11 | 66 | Thurcroft | THURCROFT | S66 9HY | LTW (DFES) | 1.2322 | 1.1902 | 1.1322 | 1.0652 | 0.99015 | 0.87115 | 0.75015 | 0.60315 | 0.45015 | 0.29215 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWHALL ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 2RS | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4053 | 1.3543 | 1.3023 | 1.0263 | 0.7543 | 0.5063 | 0.3033 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 1 | 11 | 33 | Hull West | CREYKE BECK | HU15 2QU | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 2 | 11 | 33 | Osgodby 3/4 | DRAX | HU15 2QU | LTW (DFES) | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NINELANDS LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS25 2PE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORFOLK PARK | 11 | 33 | Norton Lees | NORTON LEES | S2 3UU | LTW (DFES) | 0.62939 | 0.57439 | 0.50639 | 0.42639 | 0.33439 | 0.17839 | 0.018393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORMANBY | 11 | 33 | Blyton | KEADBY | LN8 2HQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORMANTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF6 2JA | LTW (DFES) | 4.6267 | 4.5727 | 4.4987 | 4.4127 | 4.3157 | 4.1627 | 4.0077 | 3.8207 | 3.6257 | 3.4227 | 2.3247 | 1.3197 | 0.3597 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORTH AVENUE | 11 | 33 | Menston | BRADFORD WEST | LS21 1SX | LTW (DFES) | 19.2326 | 19.1856 | 19.1266 | 19.0566 | 18.9766 | 18.8436 | 18.7076 | 18.5436 | 18.3746 | 18.2026 | 17.2876 | 16.3976 | 15.5796 | 14.9076 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORTH THORESBY | 11 | 33 | Wold Newton | KEADBY | DN36 5SB | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORWOOD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 9JR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OAKES ROAD | 11 | 33 | Lindley | ELLAND | HD3 3EW | LTW (DFES) | 2.5548 | 2.4978 | 2.4258 | 2.3408 | 2.2448 | 2.0818 | 1.9168 | 1.7158 | 1.5098 | 1.2988 | 0.17882 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OAKWOOD LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 3LF | LTW (DFES) | 19.5901 | 19.5481 | 19.4951 | 19.4321 | 19.3611 | 19.2411 | 19.1191 | 18.9731 | 18.8221 | 18.6671 | 17.8471 | 17.0511 | 16.3191 | 15.7161 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ODSAL | 11 | 33 | Staygate | SKELTON GRANGE | BD6 1BW | LTW (DFES) | 2.7076 | 2.6556 | 2.5906 | 2.5146 | 2.4266 | 2.2776 | 2.1266 | 1.9436 | 1.7556 | 1.5636 | 0.5516 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OLYMPIA MILLS | 11 | 33 | Osgodby 3/4 | DRAX | YO8 7AG | LTW (DFES) | 19.8111 | 19.7231 | 19.5931 | 19.4431 | 19.2841 | 19.0501 | 18.8061 | 18.5061 | 18.1801 | 17.8291 | 15.8521 | 14.1271 | 12.3851 | 10.8251 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ORGREAVE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 9NA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OUTWOOD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF3 3TA | LTW (DFES) | 1.8437 | 1.7877 | 1.7137 | 1.6267 | 1.5277 | 1.3697 | 1.2097 | 1.0157 | 0.81366 | 0.60666 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK HILL | 11 | 33 | Sheffield City | SHEFFIELD CITY | S2 5QY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4152 | 1.3352 | 1.2542 | 0.82623 | 0.40323 | 0.018226 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK ROAD | 11 | 33 | Thornhill 132kV | ELLAND | WF12 9LW | LTW (DFES) | 1.2008 | 1.1538 | 1.0948 | 1.0258 | 0.94583 | 0.81283 | 0.67683 | 0.51183 | 0.34283 | 0.16983 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK STREET | 11 | 132 | Park Street | WEST MELTON / THORPE MARSH | S61 1TF | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PASTURE ROAD SOUTH | 11 | 33 | Santon | KEADBY | DN18 5RX | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PATRINGTON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0AD | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 6BG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 2FL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PLANGEO | 11 | 33 | Hull South | CREYKE BECK | HU3 6EG | LTW (DFES) | 3.6054 | 3.5474 | 3.4764 | 3.3914 | 3.2944 | 3.1284 | 2.9604 | 2.7574 | 2.5514 | 2.3424 | 1.2434 | 0.15737 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | POLLINGTON | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | DN14 0RR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0JG | LTW (DFES) | 1.7478 | 1.7338 | 1.7158 | 1.6948 | 1.6718 | 1.6318 | 1.5918 | 1.5428 | 1.4928 | 1.4418 | 1.1698 | 0.90676 | 0.66376 | 0.46376 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | POOL | 11 | 33 | Menston | BRADFORD WEST | LS21 1RP | LTW (DFES) | 16.3965 | 16.3845 | 16.3675 | 16.3485 | 16.3275 | 16.2945 | 16.2625 | 16.2225 | 16.1805 | 16.1365 | 15.8945 | 15.6835 | 15.4745 | 15.2955 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PRINCE OF WALES | 11 | 33 | Featherstone | FERRYBRIDGE B | WF8 4PR | LTW (DFES) | 10.9015 | 10.8395 | 10.7545 | 10.6565 | 10.5455 | 10.3705 | 10.1935 | 9.9785 | 9.7555 | 9.5245 | 8.2685 | 7.1185 | 6.0205 | 5.0955 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PROSPECT ROAD | 11 | 33 | Lindley | ELLAND | HD3 4UY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | QUEENS ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 2LZ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | QUEENSBURY | 11 | 33 | Holmfield | BRADFORD WEST | HX3 7TJ | LTW (DFES) | 25.5604 | 25.4894 | 25.4034 | 25.3004 | 25.1834 | 24.9844 | 24.7804 | 24.5334 | 24.2794 | 24.0184 | 22.6374 | 21.2704 | 20.0194 | 18.9884 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWCLIFFE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8PQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWDON | 11 | 33 | Rodley | SKELTON GRANGE | LS19 7BZ | LTW (DFES) | 23.8956 | 23.8486 | 23.7886 | 23.7186 | 23.6386 | 23.5036 | 23.3676 | 23.2026 | 23.0326 | 22.8586 | 21.9366 | 21.0426 | 20.2186 | 19.5416 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | Rawmarsh Road 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | Rawmarsh Road 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON ROAD | 11 | 33 | Girlington | BRADFORD WEST | BD1 3SH | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON SPRING ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 1PD | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3328 | 3.2458 | 3.1558 | 2.6838 | 2.2178 | 1.7938 | 1.4468 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | REVILL LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 7QX | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROCKWARE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4RH | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY LANE | 11 | 33 | Rodley | SKELTON GRANGE | LS13 1LJ | LTW (DFES) | 0.78821 | 0.73521 | 0.66821 | 0.58921 | 0.49821 | 0.34621 | 0.19221 | 0.0062052 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROMAN AVENUE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 2DY | LTW (DFES) | 20.5246 | 20.4796 | 20.4236 | 20.3576 | 20.2816 | 20.1556 | 20.0266 | 19.8716 | 19.7126 | 19.5486 | 18.6816 | 17.8406 | 17.0666 | 16.4296 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROYDS LANE | 11 | 33 | Wakefield North | SKELTON GRANGE | LS26 0BE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | LTW (DFES) | 11.9208 | 11.9028 | 11.8808 | 11.8548 | 11.8258 | 11.7758 | 11.7258 | 11.6638 | 11.6018 | 11.5368 | 11.1948 | 10.8608 | 10.5538 | 10.3008 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT STREET | 11 | 33 | Girlington | BRADFORD WEST | BD7 4EH | LTW (DFES) | 12.4446 | 12.4136 | 12.3756 | 12.3306 | 12.2786 | 12.1906 | 12.1016 | 11.9936 | 11.8836 | 11.7706 | 11.1756 | 10.5886 | 10.0536 | 9.6156 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTERFORTH | 11 | 33 | Silsden | BRADFORD WEST | BB18 6JD | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTERHEBBLE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX3 0QH | LTW (DFES) | 19.5816 | 19.5276 | 19.4616 | 19.3846 | 19.2966 | 19.1466 | 18.9916 | 18.8036 | 18.6086 | 18.4086 | 17.3466 | 16.2896 | 15.3196 | 14.5146 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTSHOUSE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU8 9HR | LTW (DFES) | 21.3762 | 21.3392 | 21.2932 | 21.2382 | 21.1752 | 21.0672 | 20.9582 | 20.8272 | 20.6932 | 20.5582 | 19.8462 | 19.1422 | 18.5052 | 17.9902 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SANDHILL LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO41 4DF | LTW (DFES) | 0.3197 | 0.3007 | 0.2737 | 0.2417 | 0.2087 | 0.1567 | 0.1037 | 0.037702 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAXON ROAD | 11 | 33 | Norton Lees | NORTON LEES | S8 0XQ | LTW (DFES) | 2.2832 | 2.2302 | 2.1652 | 2.0892 | 2.0002 | 1.8502 | 1.6972 | 1.5122 | 1.3232 | 1.1302 | 0.11318 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCARTHO | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN33 3JL | LTW (DFES) | 0.17635 | 0.052354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCHOLES | 11 | 33 | Thornhill 132kV | ELLAND | HD9 1UG | LTW (DFES) | 0.92013 | 0.88113 | 0.83313 | 0.77613 | 0.71113 | 0.60113 | 0.48913 | 0.35413 | 0.21513 | 0.073129 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCISSETT | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCULCOATES A | 11 | 132 | Sculcoates A | CREYKE BECK | HU5 1DA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SEACROFT | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 1LU | LTW (DFES) | 13.215 | 13.179 | 13.134 | 13.081 | 13.02 | 12.919 | 12.816 | 12.691 | 12.563 | 12.432 | 11.736 | 11.061 | 10.439 | 9.928 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SEATON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU11 5RQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SELBY | 11 | 33 | Osgodby 3/4 | DRAX | YO8 8NB | LTW (DFES) | 0.67857 | 0.53157 | 0.31357 | 0.064572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SELBY ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS15 0QE | LTW (DFES) | 20.0016 | 19.9426 | 19.8676 | 19.7796 | 19.6786 | 19.5116 | 19.3396 | 19.1336 | 18.9216 | 18.7036 | 17.5496 | 16.4306 | 15.3996 | 14.5526 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHARLSTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF4 1BE | LTW (DFES) | 12.0467 | 11.9777 | 11.8847 | 11.7747 | 11.6527 | 11.4597 | 11.2637 | 11.0277 | 10.7807 | 10.5247 | 9.1377 | 7.8677 | 6.6557 | 5.6337 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHEPCOTE TINSLEY | 11 | 33 | Wincobank | WINCOBANK | S9 1RF | LTW (DFES) | 30.0977 | 30.0977 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHERBURN | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6PL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHIPLEY | 11 | 33 | Bradford | BRADFORD WEST | DN21 5UT | LTW (DFES) | 25.9345 | 25.8965 | 25.8495 | 25.7945 | 25.7305 | 25.6225 | 25.5125 | 25.3805 | 25.2435 | 25.1045 | 24.3715 | 23.6485 | 22.9885 | 22.4495 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHIRLAND LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3GD | LTW (DFES) | 0.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILVER STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 2DU | LTW (DFES) | 2.7643 | 2.7553 | 2.7453 | 2.7333 | 2.7193 | 2.6953 | 2.6713 | 2.6423 | 2.6123 | 2.5823 | 2.4213 | 2.2623 | 2.1173 | 1.9993 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILVERWOOD | 11 | 66 | Thurcroft | THURCROFT | S65 4PR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SKILLINGS LANE | 11 | 33 | Hull West | CREYKE BECK | HU15 1EQ | LTW (DFES) | 2.3834 | 2.3334 | 2.2624 | 2.1804 | 2.0924 | 1.9604 | 1.8234 | 1.6544 | 1.4714 | 1.2754 | 0.17639 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SKIPTON | 11 | 33 | Silsden | BRADFORD WEST | BD23 2RR | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SLAITHWAITE | 11 | 33 | Lindley | ELLAND | HD7 6LS | LTW (DFES) | 0.79986 | 0.76086 | 0.71186 | 0.65486 | 0.58886 | 0.47886 | 0.36586 | 0.22986 | 0.089862 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SLEDMERE GARTH | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 5DS | LTW (DFES) | 18.748 | 18.725 | 18.695 | 18.659 | 18.619 | 18.551 | 18.483 | 18.4 | 18.315 | 18.227 | 17.764 | 17.315 | 16.901 | 16.561 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SMITH STREET | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 2RY | LTW (DFES) | 12.7359 | 12.6989 | 12.6499 | 12.5919 | 12.5269 | 12.4239 | 12.3189 | 12.1909 | 12.0589 | 11.9229 | 11.1859 | 10.5019 | 9.8539 | 9.3119 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SMITHY GREEN | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SNAITHING PARK ROAD | 11 | 33 | Norton Lees | NORTON LEES | S10 3LJ | LTW (DFES) | 0.14532 | 0.098323 | 0.041323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SNELSINS LANE | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 3UH | LTW (DFES) | 16.3656 | 16.3296 | 16.2846 | 16.2316 | 16.1706 | 16.0696 | 15.9656 | 15.8396 | 15.7106 | 15.5786 | 14.8776 | 14.1916 | 13.5626 | 13.0446 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH ELMSALL | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 2JH | LTW (DFES) | 23.1644 | 23.1174 | 23.0534 | 22.9794 | 22.8954 | 22.7634 | 22.6294 | 22.4674 | 22.2984 | 22.1234 | 21.1724 | 20.3014 | 19.4704 | 18.7694 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH FERRIBY | 11 | 33 | Santon | KEADBY | DN18 6JL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH KIRKBY | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 3TJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH RESTON | 11 | 33 | Wold Newton | KEADBY | LN11 8JQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH STREET | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 1AH | LTW (DFES) | 7.6779 | 7.6349 | 7.5809 | 7.5169 | 7.4439 | 7.3209 | 7.1949 | 7.0419 | 6.8859 | 6.7269 | 5.8859 | 5.0569 | 4.3009 | 3.6819 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHGATE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 3BE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 19.1796 | 19.0496 | 18.8886 | 18.7136 | 18.5266 | 17.4796 | 16.5496 | 15.6196 | 14.7916 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHWOOD ROAD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU16 5AN | LTW (DFES) | 0.10651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EN | LTW (DFES) | 24.2002 | 24.1382 | 24.0632 | 23.9752 | 23.8742 | 23.7022 | 23.5262 | 23.3112 | 23.0892 | 22.8592 | 21.6462 | 20.4392 | 19.3322 | 18.4122 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPARK MILL LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 0TT | LTW (DFES) | 5.8932 | 5.7772 | 5.6092 | 5.4162 | 5.2102 | 4.9002 | 4.5772 | 4.1812 | 3.7512 | 3.2902 | 0.71021 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPENBOROUGH | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 5BT | LTW (DFES) | 16.5625 | 16.5085 | 16.4415 | 16.3625 | 16.2725 | 16.1195 | 15.9645 | 15.7775 | 15.5845 | 15.3855 | 14.3375 | 13.3115 | 12.3695 | 11.5935 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPRING MILL STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD5 7HF | LTW (DFES) | 3.4958 | 3.4728 | 3.4438 | 3.4098 | 3.3708 | 3.3048 | 3.2378 | 3.1558 | 3.0728 | 2.9868 | 2.5368 | 2.0938 | 1.6888 | 1.3578 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAINFORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN7 5HG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAIRFOOT | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 5AD | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STANLEY STREET | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S3 8HG | LTW (DFES) | 3.1163 | 3.1003 | 3.0803 | 3.0573 | 3.0303 | 2.9843 | 2.9383 | 2.8813 | 2.8243 | 2.7653 | 2.4563 | 2.1503 | 1.8713 | 1.6443 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STANNINGTON ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 5FH | LTW (DFES) | 1.7906 | 1.7126 | 1.6156 | 1.5006 | 1.3686 | 1.1446 | 0.91662 | 0.64162 | 0.35962 | 0.070625 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STATION ROAD | 11 | 33 | Scunthorpe North | KEADBY | DN15 6BT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STEVENSON ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 3XG | LTW (DFES) | 1.1752 | 1.1752 | 1.1752 | 1.1752 | 1.1752 | 1.1742 | 1.1742 | 1.1742 | 1.1732 | 1.1732 | 1.1712 | 1.1702 | 1.1682 | 1.1672 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOKE STREET | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3QN | LTW (DFES) | 0.146 | 0.145 | 0.145 | 0.144 | 0.144 | 0.143 | 0.141 | 0.14 | 0.139 | 0.137 | 0.129 | 0.122 | 0.115 | 0.109 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 132/11KV | 11 | 132 | Stourton 132/11kV | SKELTON GRANGE | LS10 1SP | LTW (DFES) | 1.2741 | 1.2721 | 1.2711 | 1.2681 | 1.2661 | 1.2621 | 1.2581 | 1.2531 | 1.2481 | 1.2431 | 1.2161 | 1.1891 | 1.1651 | 1.1451 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 33/11KV | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1AX | LTW (DFES) | 5.608 | 5.586 | 5.558 | 5.525 | 5.487 | 5.425 | 5.361 | 5.284 | 5.205 | 5.124 | 4.694 | 4.277 | 3.892 | 3.577 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOW | 11 | 33 | Blyton | KEADBY | LN1 2AJ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWAN BANK LANE | 11 | 33 | Halifax 132/33kV | ELLAND | HX3 9XT | LTW (DFES) | 1.3993 | 1.3623 | 1.3173 | 1.2633 | 1.2033 | 1.1003 | 0.99535 | 0.86635 | 0.73335 | 0.59535 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWEET STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9TZ | LTW (DFES) | 7.65 | 7.644 | 7.636 | 7.627 | 7.616 | 7.599 | 7.581 | 7.56 | 7.537 | 7.515 | 7.394 | 7.278 | 7.17 | 7.082 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWINNOW MOOR | 11 | 33 | Rodley | SKELTON GRANGE | LS13 4RJ | LTW (DFES) | 2.3665 | 2.3125 | 2.2445 | 2.1645 | 2.0725 | 1.9195 | 1.7645 | 1.5765 | 1.3835 | 1.1855 | 0.13647 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TADCASTER | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9PA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TANKERSLEY PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 2PT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S60 1AD | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNBURY | 11 | 33 | Rodley | SKELTON GRANGE | BD3 7AD | LTW (DFES) | 5.0153 | 4.9733 | 4.9203 | 4.8583 | 4.7863 | 4.6653 | 4.5423 | 4.3943 | 4.2413 | 4.0853 | 3.2633 | 2.4543 | 1.7153 | 1.1103 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN8 4NA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNTON | 11 | 33 | Holmfield | BRADFORD WEST | BD13 3DP | LTW (DFES) | 19.9722 | 19.9002 | 19.8112 | 19.7062 | 19.5862 | 19.3822 | 19.1732 | 18.9222 | 18.6642 | 18.4012 | 17.0122 | 15.6442 | 14.3952 | 13.3732 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORPE ROAD | 11 | 33 | Osgodby 3/4 | DRAX | DN14 7PA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TICKHILL ROAD | 11 | 66 | Thurcroft | THURCROFT | S66 7QN | LTW (DFES) | 29.0744 | 29.0064 | 28.9134 | 28.8054 | 28.6844 | 28.4944 | 28.3004 | 28.0654 | 27.8194 | 27.5644 | 26.1774 | 24.9044 | 23.6864 | 22.6554 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINGLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | WF3 1SS | LTW (DFES) | 0.10361 | 0.053615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY PARK ROAD | 11 | 33 | Wincobank | WINCOBANK | S9 5DL | LTW (DFES) | 2.8587 | 2.8557 | 2.8517 | 2.8467 | 2.8417 | 2.8327 | 2.8227 | 2.8117 | 2.7997 | 2.7877 | 2.7257 | 2.6637 | 2.6077 | 2.5617 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1TY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TIVERTON ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 4DA | LTW (DFES) | 1.4561 | 1.4151 | 1.3641 | 1.3041 | 1.2351 | 1.1161 | 0.99614 | 0.85114 | 0.70414 | 0.55414 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TODMORDEN | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | OL14 7NB | LTW (DFES) | 12.813 | 12.772 | 12.722 | 12.663 | 12.596 | 12.481 | 12.363 | 12.22 | 12.072 | 11.919 | 11.109 | 10.303 | 9.564 | 8.951 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TOLLER LANE | 11 | 33 | Girlington | BRADFORD WEST | BD9 5LE | LTW (DFES) | 21.2862 | 21.2422 | 21.1872 | 21.1232 | 21.0492 | 20.9242 | 20.7962 | 20.6422 | 20.4842 | 20.3232 | 19.4722 | 18.6332 | 17.8682 | 17.2412 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TONG STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9PP | LTW (DFES) | 3.2652 | 3.2412 | 3.2132 | 3.1782 | 3.1392 | 3.0732 | 3.0052 | 2.9232 | 2.8392 | 2.7532 | 2.3012 | 1.8552 | 1.4482 | 1.1152 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | UPPER BASINGHALL STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS1 5JS | LTW (DFES) | 4.337 | 4.333 | 4.328 | 4.323 | 4.317 | 4.306 | 4.295 | 4.282 | 4.269 | 4.255 | 4.183 | 4.113 | 4.049 | 3.995 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | VARLEY STREET | 11 | 33 | Rodley | SKELTON GRANGE | LS28 6AN | LTW (DFES) | 22.6994 | 22.6514 | 22.5914 | 22.5204 | 22.4384 | 22.3034 | 22.1644 | 21.9974 | 21.8264 | 21.6504 | 20.7184 | 19.8134 | 18.9804 | 18.2954 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | VICTORIA STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4DP | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50542 | 0.46742 | 0.42742 | 0.22142 | 0.016419 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WALESBY | 11 | 33 | Wold Newton | KEADBY | LN8 3UL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WARREN LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9NT | LTW (DFES) | 3.8798 | 3.8668 | 3.8498 | 3.8308 | 3.8088 | 3.7728 | 3.7358 | 3.6908 | 3.6448 | 3.5978 | 3.3428 | 3.0988 | 2.8718 | 2.6818 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WATH UPON DEARNE | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DX | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | Wincobank | WINCOBANK | S60 5BL | LTW (DFES) | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5026 | 30.5026 | 30.5016 | 30.5006 | 30.4996 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAWNE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 5BT | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEELAND ROAD | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 0LA | LTW (DFES) | 7.1731 | 7.1501 | 7.1181 | 31.2286 | 31.1866 | 31.1216 | 31.0546 | 30.9736 | 30.8896 | 30.8026 | 30.3306 | 29.8976 | 29.4846 | 29.1356 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WELLINGTON STREET | 11 | 33 | Featherstone | FERRYBRIDGE B | WF10 1NW | LTW (DFES) | 12.9371 | 12.8981 | 12.8441 | 12.7821 | 12.7121 | 12.6021 | 12.4891 | 12.3541 | 12.2131 | 12.0661 | 11.2721 | 10.5451 | 9.8511 | 9.2661 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WESLEY CRESCENT | 11 | 33 | Humberston | GRIMSBY WEST | DN35 0JU | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST DOCKS | 11 | 33 | Hull South | CREYKE BECK | HU3 4UU | LTW (DFES) | 1.7763 | 1.7743 | 1.7723 | 1.7693 | 1.7663 | 1.7603 | 1.7553 | 1.7483 | 1.7413 | 1.7343 | 1.6983 | 1.6633 | 1.6313 | 1.6053 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST END LANE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN11 0PU | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST MOOR PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3FE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST PARK | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 5PS | LTW (DFES) | 7.0866 | 7.0486 | 7.0006 | 6.9436 | 6.8786 | 6.7706 | 6.6606 | 6.5276 | 6.3916 | 6.2506 | 5.5086 | 4.7886 | 4.1256 | 3.5796 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WESTCOTT STREET | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU8 8JN | LTW (DFES) | 0.98289 | 0.91389 | 0.83089 | 0.73089 | 0.61589 | 0.42089 | 0.22189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHEATACRE ROAD | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 2GQ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHEATLEY PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4PG | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHINGATE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 3QT | LTW (DFES) | 19.8881 | 19.8561 | 19.8171 | 19.7701 | 19.7161 | 19.6271 | 19.5361 | 19.4261 | 19.3131 | 19.1981 | 18.5841 | 17.9891 | 17.4411 | 16.9911 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITE LEE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 8AF | LTW (DFES) | 1.9435 | 1.8775 | 1.7945 | 1.6965 | 1.5845 | 1.3965 | 1.2055 | 0.9735 | 0.7355 | 0.4905 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | Low Road | SKELTON GRANGE | LS1 4HR | LTW (DFES) | 7.776 | 7.774 | 7.772 | 7.769 | 7.767 | 7.762 | 7.757 | 7.751 | 7.745 | 7.739 | 7.706 | 7.675 | 7.646 | 7.622 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS1 4BN | LTW (DFES) | 18.7039 | 18.7009 | 18.6979 | 18.6939 | 18.6889 | 18.6809 | 18.6739 | 18.6639 | 18.6549 | 18.6449 | 18.5919 | 18.5419 | 18.4949 | 18.4559 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WIBSEY | 11 | 33 | Staygate | SKELTON GRANGE | BD6 3BG | LTW (DFES) | 0.62126 | 0.55926 | 0.48126 | 0.38926 | 0.28426 | 0.10626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WITHERNSEA | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU19 2QA | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOODCOCK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 5LL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOODSEATS | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 8QB | LTW (DFES) | 2.2207 | 2.1707 | 2.1087 | 2.0357 | 1.9517 | 1.8097 | 1.6637 | 1.4887 | 1.3087 | 1.1257 | 0.15969 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOOLLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 5JE | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WORSBROUGH PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S70 5LY | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WRAWBY | 11 | 33 | Santon | KEADBY | DN20 8SX | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4BL | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YEW GREEN ROAD | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD4 5DD | LTW (DFES) | 1.373 | 1.325 | 1.265 | 1.194 | 1.114 | 0.97897 | 0.83997 | 0.67397 | 0.50197 | 0.32597 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YORK ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 6TF | LTW (DFES) | 20.7971 | 20.7391 | 20.6671 | 20.5821 | 20.4841 | 20.3221 | 20.1561 | 19.9561 | 19.7511 | 19.5401 | 18.4231 | 17.3391 | 16.3421 | 15.5211 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YORK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 3AZ | LTW (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Leading the Way (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ANNFIELD | 66 | 132 | Annfield | STELLA SOUTH | DH9 7XW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BARRACK ROAD | 33 | 132 | Barrack Road | STELLA NORTH | NE4 6DB | SP (DFES) | 114.54 | 114.05 | 113.958 | 113.866 | 113.773 | 113.668 | 113.546 | 113.432 | 113.319 | 113.18 | 112.373 | 111.915 | 111.524 | 110.852 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER | 33 | 132 | Blucher | STELLA NORTH | NE15 9SD | SP (DFES) | 94.254 | 93.662 | 93.439 | 93.217 | 93.045 | 92.847 | 92.624 | 92.389 | 92.13 | 91.831 | 90.211 | 88.875 | 87.692 | 86.519 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD | 33 | 132 | Bowesfield | NORTON | TS18 3HP | SP (DFES) | 59.48 | 56.066 | 54.908 | 53.767 | 53.138 | 52.5 | 51.875 | 51.308 | 50.698 | 49.998 | 45.868 | 43.947 | 42.668 | 41.854 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CHIRTON GRANGE | 33 | 132 | Chirton Grange | TYNEMOUTH | NE29 8EY | SP (DFES) | 61.929 | 61.344 | 61.161 | 60.977 | 60.811 | 60.618 | 60.393 | 60.159 | 59.905 | 59.608 | 57.985 | 56.68 | 55.507 | 54.189 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | COALBURNS | 66 | 132 | Coalburns | STELLA SOUTH | NE40 4JP | SP (DFES) | 67.098 | 63.551 | 62.36 | 61.19 | 60.619 | 60.069 | 59.573 | 59.165 | 58.734 | 58.247 | 55.217 | 54.484 | 54.409 | 54.993 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL | 33 | 132 | Darlington Central | NORTON | DL1 1HG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON NORTH | 33 | 132 | Darlington North | NORTON | DL3 0XE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON | 66 | 132 | Dunston | STELLA NORTH | NE11 9DH | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH | 33 | 132 | Flatworth | TYNEMOUTH | NE29 7FN | SP (DFES) | 27.306 | 27.076 | 26.997 | 26.917 | 26.839 | 26.747 | 26.638 | 26.521 | 26.392 | 26.243 | 25.439 | 24.741 | 24.103 | 23.409 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH | 33 | 132 | Gosforth | TYNEMOUTH | NE3 1XL | SP (DFES) | 88.893 | 88.423 | 88.271 | 88.118 | 87.973 | 87.801 | 87.6 | 87.386 | 87.154 | 86.884 | 85.422 | 84.186 | 83.065 | 81.819 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/33KV | 33 | 132 | Harrogate 132/33kV | KNARESBOROUGH | HG1 2LA | SP (DFES) | 45.541 | 44.708 | 44.435 | 44.164 | 43.972 | 43.76 | 43.529 | 43.298 | 43.048 | 42.757 | 41.122 | 40.003 | 39.051 | 38.065 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE | 33 | 132 | Husthwaite | KNARESBOROUGH | YO61 4PN | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | Leeming Bar_Skeeby | NORTON | DL7 0RL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LINTON | 66 | 132 | Linton | BLYTH 132kV | NE61 5DA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALTON GRID | 66 | 132 | Malton Grid | OSBALDWICK | YO17 6RD | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 132/33kV | 33 | 132 | Melrosegate | OSBALDWICK | YO31 0YB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES | 66 | 132 | North Tees | NORTON | TS23 1PY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE 132/66kV | 66 | 132 | Potter House | SPENNYMOOR | DH1 5FF | SP (DFES) | 88.321 | 86.561 | 85.979 | 85.403 | 85.041 | 84.658 | 84.258 | 83.874 | 83.458 | 82.975 | 80.179 | 78.581 | 77.3 | 76.083 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSWORTH | 66 | 132 | Ravensworth | STELLA SOUTH | DH3 1RQ | SP (DFES) | 75.999 | 75.34 | 75.139 | 74.94 | 74.814 | 74.681 | 74.543 | 74.415 | 74.279 | 74.119 | 73.178 | 72.701 | 72.332 | 71.935 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH GRID | 33 | 132 | Scarborough Grid | OSBALDWICK | YO11 2YH | SP (DFES) | 69.325 | 66.255 | 65.304 | 64.366 | 63.83 | 63.282 | 62.74 | 62.263 | 61.768 | 61.198 | 57.852 | 56.301 | 55.367 | 54.539 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEAL SANDS | 66 | 132 | Seal Sands | SALTHOLME | TS2 1FB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5LJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO | 66 | 132 | Toronto | SPENNYMOOR | DL14 7RJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 3PS | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ATTERCLIFFE | 33 | 132 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3FA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 132/66KV | 66 | 132 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1LR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6NJ | SP (DFES) | 66.8734 | 65.9934 | 64.2544 | 62.6244 | 61.1824 | 59.7784 | 58.4214 | 57.2214 | 56.0404 | 54.8794 | 50.5124 | 47.9124 | 45.3924 | 43.6064 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEVERLEY 132/33KV | 33 | 132 | Beverley 132/33kV | CREYKE BECK | HU17 0RW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 132/33KV | 33 | 132 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | SP (DFES) | 9.9806 | 9.8326 | 9.6456 | 9.4626 | 9.2886 | 9.0886 | 8.8626 | 8.6156 | 8.3396 | 8.0336 | 6.5136 | 4.9946 | 3.5386 | 2.1936 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS B | 33 | 132 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1DA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLYTON | 33 | 132 | Blyton | KEADBY | DN21 3NS | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRADFORD | 33 | 132 | Bradford | BRADFORD WEST | BD1 4RF | SP (DFES) | 99.828 | 99.679 | 99.529 | 99.377 | 99.226 | 99.038 | 98.812 | 98.547 | 98.243 | 97.898 | 96.095 | 94.19 | 92.366 | 90.649 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHAM | 33 | 132 | Bramham | FERRYBRIDGE B | LS24 9NT | SP (DFES) | 22.7167 | 18.3287 | 9.0217 | 0.34772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRANSHOLME | 33 | 132 | Bransholme | CREYKE BECK | HU7 4ZN | SP (DFES) | 65.1273 | 64.3343 | 62.7503 | 61.2663 | 59.9573 | 58.6863 | 57.4633 | 56.3913 | 55.3393 | 54.3123 | 50.5113 | 48.3523 | 46.2573 | 44.8253 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | Brighouse 132/33kV | ELLAND | HD6 1PZ | SP (DFES) | 95.1777 | 94.1297 | 92.0117 | 90.0287 | 88.2827 | 86.5947 | 84.9767 | 83.5667 | 82.1927 | 80.8577 | 76.0017 | 73.3557 | 70.7927 | 69.1107 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 8UX | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER CENTRAL | 33 | 132 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1RE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | Driffield/Beverley Group | CREYKE BECK | YO25 5NW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FEATHERSTONE | 33 | 132 | Featherstone | FERRYBRIDGE B | WF7 6HE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIRLINGTON | 33 | 132 | Girlington | BRADFORD WEST | BD7 2NB | SP (DFES) | 85.3435 | 85.2535 | 85.1625 | 85.0715 | 84.9795 | 84.8655 | 84.7295 | 84.5695 | 84.3855 | 84.1765 | 83.0855 | 81.9345 | 80.8305 | 79.7925 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 132/33KV | 33 | 132 | Halifax 132/33kV | ELLAND | HX1 1XB | SP (DFES) | 1.5196 | 1.4706 | 1.4206 | 1.3706 | 1.3206 | 1.2596 | 1.1866 | 1.0996 | 0.99962 | 0.88662 | 0.29662 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HECKMONDWIKE | 33 | 132 | Heckmondwike | SKELTON GRANGE | WF16 9LU | SP (DFES) | 88.912 | 88.809 | 88.705 | 88.6 | 88.495 | 88.365 | 88.21 | 88.027 | 87.816 | 87.577 | 86.325 | 85.011 | 83.751 | 82.565 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLMFIELD | 33 | 132 | Holmfield | BRADFORD WEST | HX2 9AY | SP (DFES) | 57.4245 | 57.2605 | 57.0955 | 56.9275 | 56.7625 | 56.5575 | 56.3115 | 56.0215 | 55.6885 | 55.3115 | 53.3415 | 51.2555 | 49.2605 | 47.3855 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 132/33KV | 33 | 132 | Hull East 132/33kV | SALTEND NORTH | HU9 5NL | SP (DFES) | 8.8107 | 8.6597 | 8.4997 | 8.3407 | 8.1897 | 8.0087 | 7.7947 | 7.5467 | 7.2617 | 6.9367 | 5.2237 | 3.5787 | 1.9707 | 0.46973 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL SOUTH | 33 | 132 | Hull South | CREYKE BECK | HU3 5JA | SP (DFES) | 88.5962 | 88.4562 | 88.3172 | 88.1752 | 88.0352 | 87.8612 | 87.6522 | 87.4062 | 87.1222 | 86.8002 | 85.1062 | 83.3502 | 81.6602 | 80.0692 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL WEST | 33 | 132 | Hull West | CREYKE BECK | HU13 0FA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUMBERSTON | 33 | 132 | Humberston | GRIMSBY WEST | DN36 4AW | SP (DFES) | 67.4631 | 67.1481 | 66.5801 | 66.0431 | 65.5621 | 65.0811 | 64.6001 | 64.1521 | 63.6941 | 63.2271 | 61.2751 | 59.8631 | 58.4881 | 57.3671 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNNINGLEY | 33 | 132 | Hunningley | WEST MELTON SECTION 3 | S70 3ET | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNSHELF | 66 | 132 | Hunshelf | WEST MELTON SECTION 3 | S36 8WR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IMMINGHAM | 33 | 132 | Immingham | GRIMSBY WEST | DN40 1QT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKHAW LANE | 33 | 132 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8SB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C 2/5 | 33 | 132 | Kirkstall C 2/5 | KIRKSTALL B | LS18 4EL | SP (DFES) | 81.9742 | 81.9442 | 81.9142 | 81.8832 | 81.8532 | 81.8152 | 81.7702 | 81.7172 | 81.6562 | 81.5862 | 81.2232 | 80.8432 | 80.4782 | 80.1342 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS18 4EL | SP (DFES) | 106.5055 | 106.0675 | 105.3445 | 104.6565 | 104.0315 | 103.3815 | 102.7095 | 102.0505 | 101.3575 | 100.6295 | 97.3795 | 94.6325 | 91.9845 | 89.6855 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS EAST | 33 | 132 | Leeds East | SKELTON GRANGE | LS9 6ED | SP (DFES) | 65.5952 | 64.9412 | 63.6862 | 62.5072 | 61.4602 | 60.4302 | 59.4242 | 58.5182 | 57.6142 | 56.7152 | 53.2042 | 50.9102 | 48.6912 | 47.0122 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS NORTH | 33 | 132 | Leeds North | SKELTON GRANGE | LS7 2AU | SP (DFES) | 107.988 | 107.893 | 107.798 | 107.702 | 107.606 | 107.487 | 107.344 | 107.176 | 106.982 | 106.763 | 105.611 | 104.409 | 103.253 | 102.165 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LINDLEY | 33 | 132 | Lindley | ELLAND | HD3 3NY | SP (DFES) | 92.3762 | 91.8582 | 90.9142 | 90.0232 | 89.2272 | 88.4282 | 87.6322 | 86.8932 | 86.1402 | 85.3742 | 82.2152 | 79.8772 | 77.6222 | 75.7902 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOW ROAD | 33 | 132 | Low Road | SKELTON GRANGE | LS10 1RH | SP (DFES) | 1.746 | 1.618 | 1.431 | 1.251 | 1.083 | 0.90202 | 0.70602 | 0.50302 | 0.28302 | 0.045016 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MALLARD WAY | 33 | 132 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MENSTON | 33 | 132 | Menston | BRADFORD WEST | LS29 6BP | SP (DFES) | 86.1707 | 85.0667 | 82.7917 | 80.6667 | 78.7987 | 77.0037 | 75.2967 | 73.8297 | 72.4117 | 71.0487 | 66.2427 | 63.8937 | 61.6077 | 60.2547 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOSS ROAD | 33 | 132 | Moss Road | GRIMSBY WEST | DN32 0LW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 1/2 | 33 | 132 | Osgodby 1/2 | DRAX | YO8 5HY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 3/4 | 33 | 132 | Osgodby 3/4 | DRAX | YO8 5HY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY | 33 | 132 | Rodley | SKELTON GRANGE | LS13 1PZ | SP (DFES) | 121.1751 | 120.3651 | 118.7751 | 117.2831 | 115.9631 | 114.6741 | 113.4261 | 112.3181 | 111.2251 | 110.1481 | 106.0661 | 103.5811 | 101.1751 | 99.4441 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | SP (DFES) | 81.3358 | 81.1848 | 81.0008 | 80.8208 | 80.6478 | 80.4468 | 80.2188 | 79.9658 | 79.6818 | 79.3658 | 77.7758 | 76.1828 | 74.6528 | 73.2348 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTEND 132/33KV | 33 | 132 | Saltend 132/33kV | SALTEND NORTH | HU12 8EY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SANTON | 33 | 132 | Santon | KEADBY | DN16 1XP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE NORTH | 33 | 132 | Scunthorpe North | KEADBY | DN15 8GN | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE SOUTH | 33 | 132 | Scunthorpe South | KEADBY | DN16 1BD | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILSDEN | 33 | 132 | Silsden | BRADFORD WEST | BD20 0ND | SP (DFES) | 0 | 51.3477 | 48.1737 | 45.1977 | 42.5997 | 40.0717 | 37.6297 | 35.4707 | 33.3387 | 31.2437 | 23.3657 | 18.7487 | 14.3057 | 11.2227 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EL | SP (DFES) | 59.6234 | 59.2994 | 58.7514 | 58.2314 | 57.7624 | 57.2794 | 56.7844 | 56.3054 | 55.8044 | 55.2834 | 53.0034 | 51.1034 | 49.2824 | 47.7224 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAYGATE | 33 | 132 | Staygate | SKELTON GRANGE | BD6 1YA | SP (DFES) | 116.1327 | 116.0137 | 115.8947 | 115.7737 | 115.6527 | 115.5037 | 115.3237 | 115.1127 | 114.8697 | 114.5947 | 113.1587 | 111.6417 | 110.1887 | 108.8207 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNHILL 132KV | 33 | 132 | Thornhill 132kV | ELLAND | WF13 3JQ | SP (DFES) | 19.1227 | 18.0507 | 15.9597 | 13.9977 | 12.2607 | 10.5617 | 8.9107 | 7.4397 | 5.9817 | 4.5397 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7AL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD NORTH | 33 | 132 | Wakefield North | SKELTON GRANGE | WF1 3HN | SP (DFES) | 79.3564 | 77.9384 | 75.0544 | 72.3574 | 69.9844 | 67.6964 | 65.5104 | 63.6164 | 61.7744 | 59.9904 | 53.5554 | 50.2504 | 47.0194 | 44.9794 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST MELTON | 66 | 132 | West Melton | WEST MELTON SECTION 3 | S63 6EZ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHINMOOR | 33 | 132 | Whinmoor | FERRYBRIDGE B | LS14 2DG | SP (DFES) | 112.4473 | 110.9073 | 107.7403 | 104.7813 | 102.1803 | 99.6793 | 97.2983 | 95.2493 | 93.2673 | 91.3593 | 84.6123 | 81.2763 | 78.0303 | 76.0843 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOLD NEWTON | 33 | 132 | Wold Newton | KEADBY | DN37 0SW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4JJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ACKLAM | 11 | 33 | Bowesfield | NORTON | TS5 7LD | SP (DFES) | 15.7844 | 15.6714 | 15.6194 | 15.5664 | 15.5134 | 15.4484 | 15.3704 | 15.2824 | 15.1844 | 15.0714 | 14.4684 | 13.9074 | 13.3844 | 12.8514 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AMBERTON ROAD | 11 | 66 | Hartmoor | HARTMOOR | TS24 8PQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ANNFIELD 66/20KV | 20 | 66 | Annfield | STELLA SOUTH | DH9 7XW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ASHINGTON | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE63 8UJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE FORREST | 11 | 33 | Darlington North | NORTON | DL1 3NL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | Darlington North | NORTON | DL5 6HY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BARDEN FRIAR | 20 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5JR | SP (DFES) | 7.588 | 7.568 | 7.564 | 7.56 | 7.555 | 7.551 | 7.545 | 7.54 | 7.535 | 7.528 | 7.487 | 7.467 | 7.448 | 7.418 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BEDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 1AH | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BELMONT | 11 | 66 | Potter House | SPENNYMOOR | DH1 2HL | SP (DFES) | 2.8165 | 2.6705 | 2.6245 | 2.5785 | 2.5315 | 2.4765 | 2.4115 | 2.3405 | 2.2635 | 2.1715 | 1.6635 | 1.2705 | 0.90051 | 0.47851 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENSHAM | 11 | 66 | Dunston | STELLA NORTH | NE8 2XY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.447 | 12.391 | 12.325 | 11.969 | 11.664 | 11.379 | 11.073 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENTON SQUARE | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE12 9SR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BENWELL | 11 | 66 | Dunston | STELLA NORTH | NE4 8XQ | SP (DFES) | 12.119 | 11.986 | 11.944 | 11.901 | 11.858 | 11.806 | 11.745 | 11.68 | 11.609 | 11.526 | 11.081 | 10.696 | 10.345 | 9.95 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | North Tees | NORTON | TS23 2AL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BILLY MILL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE29 8LP | SP (DFES) | 17.3739 | 17.2829 | 17.2469 | 17.2099 | 17.1729 | 17.1279 | 17.0749 | 17.0159 | 16.9499 | 16.8739 | 16.4699 | 16.0989 | 15.7569 | 15.3969 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | SP (DFES) | 32.6512 | 32.5822 | 32.5542 | 32.5262 | 32.4972 | 32.4632 | 32.4212 | 32.3752 | 32.3242 | 32.2642 | 31.9432 | 31.6592 | 31.3932 | 31.1142 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | SP (DFES) | 24.2592 | 24.2032 | 24.1842 | 24.1662 | 24.1482 | 24.1262 | 24.0992 | 24.0712 | 24.0412 | 24.0042 | 23.8062 | 23.6452 | 23.4952 | 23.3262 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLAYDON BURN | 11 | 66 | Dunston | STELLA NORTH | NE21 4BG | SP (DFES) | 1.942 | 1.807 | 1.765 | 1.724 | 1.682 | 1.633 | 1.574 | 1.512 | 1.444 | 1.363 | 0.919 | 0.574 | 0.251 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER 33/11KV | 11 | 33 | Blucher | STELLA NORTH | NE15 9SB | SP (DFES) | 14.5262 | 14.4342 | 14.3962 | 14.3582 | 14.3192 | 14.2722 | 14.2162 | 14.1532 | 14.0842 | 14.0042 | 13.5802 | 13.1842 | 12.8192 | 12.4392 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOLDON DOWNHILL | 20 | 66 | West Boldon | WEST BOLDON | NE36 0AS | SP (DFES) | 19.3225 | 19.2595 | 19.2305 | 19.2005 | 19.1705 | 19.1335 | 19.0895 | 19.0405 | 18.9855 | 18.9215 | 18.5815 | 18.2655 | 17.9695 | 17.6695 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | YO51 9NS | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 33/11KV | 11 | 33 | Bowesfield | NORTON | TS18 3HR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 66/11KV | 11 | 66 | North Tees | NORTON | TS23 1PX | SP (DFES) | 39.3071 | 39.2201 | 39.1941 | 39.1681 | 39.1421 | 39.1111 | 39.0741 | 39.0351 | 38.9921 | 38.9421 | 38.6611 | 38.4491 | 38.2491 | 38.0161 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BRANCEPETH | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL15 0TW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BREAMISH STREET | 11 | 66 | West Boldon | WEST BOLDON | NE1 2BL | SP (DFES) | 22.453 | 22.359 | 22.339 | 22.318 | 22.298 | 22.274 | 22.245 | 22.218 | 22.19 | 22.156 | 21.966 | 21.834 | 21.718 | 21.554 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | BRENDA TRADING | 11 | 66 | Hartmoor | HARTMOOR | TS25 1PD | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CAMPLESHON ROAD | 11 | 33 | Melrosegate | OSBALDWICK | YO23 1HZ | SP (DFES) | 0.4087 | 0.2527 | 0.2077 | 0.1617 | 0.1167 | 0.061703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARLEY HILL | 11 | 66 | West Boldon | WEST BOLDON | SR5 1SG | SP (DFES) | 19.568 | 19.418 | 19.368 | 19.317 | 19.266 | 19.205 | 19.132 | 19.053 | 18.967 | 18.865 | 18.313 | 17.855 | 17.428 | 16.954 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARLIN HOW T3 T4 | 11 | 66 | Lackenby | LACKENBY | TS13 4DL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CARR HILL | 11 | 66 | West Boldon | WEST BOLDON | NE10 9SY | SP (DFES) | 20.0189 | 19.8849 | 19.8289 | 19.7719 | 19.7149 | 19.6459 | 19.5629 | 19.4709 | 19.3689 | 19.2499 | 18.6099 | 18.0379 | 17.5029 | 16.9449 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CATTERICK CAMP | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL9 3HE | SP (DFES) | 8.634 | 8.438 | 8.37 | 8.302 | 8.233 | 8.151 | 8.052 | 7.945 | 7.825 | 7.685 | 6.918 | 6.286 | 5.697 | 5.051 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CLOSE | 11 | 66 | Dunston | STELLA NORTH | NE1 3NB | SP (DFES) | 12.725 | 12.497 | 12.466 | 12.435 | 12.404 | 12.37 | 12.332 | 12.302 | 12.277 | 12.244 | 12.035 | 11.988 | 11.968 | 11.798 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CONEYTHORPE | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG5 0RZ | SP (DFES) | 6.8316 | 6.7106 | 6.6766 | 6.6426 | 6.6076 | 6.5676 | 6.5186 | 6.4676 | 6.4136 | 6.3486 | 5.9926 | 5.7136 | 5.4586 | 5.1536 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CONSETT | 20 | 66 | Annfield | STELLA SOUTH | DH8 7ND | SP (DFES) | 7.742 | 7.539 | 7.468 | 7.397 | 7.325 | 7.24 | 7.138 | 7.027 | 6.904 | 6.76 | 5.968 | 5.321 | 4.714 | 4.046 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CORPORATION STREET | 11 | 33 | Barrack Road | STELLA NORTH | NE4 5SS | SP (DFES) | 19.5675 | 19.4955 | 19.4795 | 19.4635 | 19.4475 | 19.4295 | 19.4075 | 19.3865 | 19.3655 | 19.3395 | 19.1945 | 19.0925 | 19.0045 | 18.8785 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | COWTON | 11 | 33 | Darlington Central | NORTON | DL6 2NF | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLEY | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 2PP | SP (DFES) | 9.5 | 9.423 | 9.407 | 9.39 | 9.373 | 9.354 | 9.332 | 9.309 | 9.286 | 9.258 | 9.097 | 8.997 | 8.906 | 8.775 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 132/6KV | 6 | 132 | Darlington 132/6kV | NORTON | DL1 1SW | SP (DFES) | 0 | 29.7104 | 29.6894 | 29.6684 | 29.6464 | 29.6214 | 29.5914 | 29.5604 | 29.5264 | 29.4854 | 29.2644 | 29.0884 | 28.9264 | 28.7374 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1SW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1HG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON EAST | 11 | 33 | Darlington Central | NORTON | DL1 4NP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON WEST | 11 | 33 | Darlington North | NORTON | DL3 9QG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DENWICK | 20 | 66 | Linton | BLYTH 132kV | NE66 3RG | SP (DFES) | 5.901 | 5.576 | 5.493 | 5.409 | 5.325 | 5.227 | 5.112 | 4.991 | 4.862 | 4.705 | 3.81 | 3.219 | 2.66 | 1.951 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/11KV | 11 | 66 | Dunston | STELLA NORTH | NE11 9DH | SP (DFES) | 1.3533 | 1.2593 | 1.2343 | 1.2083 | 1.1833 | 1.1533 | 1.1173 | 1.0803 | 1.0413 | 0.99428 | 0.72828 | 0.53628 | 0.35828 | 0.13828 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/20KV | 20 | 66 | Dunston | STELLA NORTH | NE11 9DH | SP (DFES) | 12.001 | 11.884 | 11.841 | 11.798 | 11.754 | 11.702 | 11.639 | 11.57 | 11.494 | 11.405 | 10.923 | 10.51 | 10.124 | 9.708 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | DURHAM EAST | 11 | 66 | Potter House | SPENNYMOOR | DH1 5SU | SP (DFES) | 22.0888 | 21.9568 | 21.9318 | 21.9068 | 21.8808 | 21.8528 | 21.8198 | 21.7878 | 21.7548 | 21.7148 | 21.4668 | 21.3548 | 21.2498 | 21.0658 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EASTFIELD | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 3BY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.0999 | 22.0259 | 21.9389 | 21.4749 | 21.0599 | 20.6859 | 20.2689 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EASTGATE CEMENT | 20 | 66 | Toronto | SPENNYMOOR | DL13 2LA | SP (DFES) | 11.643 | 11.572 | 11.556 | 11.541 | 11.525 | 11.507 | 11.486 | 11.465 | 11.443 | 11.416 | 11.258 | 11.169 | 11.085 | 10.963 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | Barrack Road | STELLA NORTH | NE5 4JQ | SP (DFES) | 22.6949 | 22.5719 | 22.5459 | 22.5189 | 22.4919 | 22.4609 | 22.4249 | 22.3899 | 22.3529 | 22.3099 | 22.0649 | 21.8949 | 21.7469 | 21.5359 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ELVINGTON | 11 | 33 | Melrosegate | OSBALDWICK | YO41 4DY | SP (DFES) | 0.9347 | 0.8707 | 0.8577 | 0.8457 | 0.8327 | 0.8187 | 0.8017 | 0.7867 | 0.7707 | 0.7517 | 0.6397 | 0.5757 | 0.5197 | 0.4267 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FARADAY STREET | 11 | 66 | North Tees | NORTON | TS1 4JG | SP (DFES) | 13.1838 | 12.9788 | 12.9218 | 12.8648 | 12.8078 | 12.7398 | 12.6608 | 12.5768 | 12.4878 | 12.3808 | 11.7898 | 11.3438 | 10.9318 | 10.4338 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | Blyth 66kV | BLYTH 66KV | NE3 2SW and NE13 6BH | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FISHBURN | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | TS29 6JQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH CENTRAL | 11 | 33 | Flatworth | TYNEMOUTH | NE29 7SH | SP (DFES) | 30.6767 | 30.5867 | 30.5627 | 30.5377 | 30.5137 | 30.4847 | 30.4497 | 30.4137 | 30.3757 | 30.3307 | 30.0837 | 29.8877 | 29.7097 | 29.4947 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FOSS ISLANDS | 11 | 33 | Melrosegate | OSBALDWICK | YO31 7US | SP (DFES) | 1.3087 | 0.9947 | 0.9317 | 0.8687 | 0.8057 | 0.7327 | 0.6487 | 0.5677 | 0.4877 | 0.3897 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FOSSWAY 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE6 4AN | SP (DFES) | 14.3759 | 14.2149 | 14.1669 | 14.1179 | 14.0679 | 14.0089 | 13.9389 | 13.8659 | 13.7859 | 13.6919 | 13.1879 | 12.7599 | 12.3709 | 11.9249 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | FYLANDS BRIDGE | 11 | 66 | Toronto | SPENNYMOOR | DL14 9TA | SP (DFES) | 9.974 | 9.83 | 9.777 | 9.723 | 9.668 | 9.602 | 9.524 | 9.438 | 9.342 | 9.229 | 8.619 | 8.103 | 7.618 | 7.097 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GALE LANE | 11 | 33 | Poppleton | POPPLETON | YO24 3AF | SP (DFES) | 7.773 | 7.688 | 7.649 | 7.609 | 7.569 | 7.519 | 7.46 | 7.394 | 7.32 | 7.234 | 6.786 | 6.354 | 5.954 | 5.55 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GARWOOD STREET | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 5DQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.3606 | 21.2926 | 21.2106 | 20.7476 | 20.4276 | 20.1386 | 19.7496 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD CENTRAL | 11 | 33 | Barrack Road | STELLA NORTH | NE8 1HB | SP (DFES) | 16.9038 | 16.8028 | 16.7808 | 16.7588 | 16.7358 | 16.7108 | 16.6808 | 16.6508 | 16.6198 | 16.5818 | 16.3618 | 16.2308 | 16.1088 | 15.9338 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD EAST | 11 | 66 | West Boldon | WEST BOLDON | NE8 3AH | SP (DFES) | 22.618 | 22.596 | 22.592 | 22.589 | 22.585 | 22.58 | 22.575 | 22.57 | 22.566 | 22.56 | 22.525 | 22.509 | 22.494 | 22.467 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE3 1RR | SP (DFES) | 30.496 | 30.415 | 30.396 | 30.376 | 30.356 | 30.333 | 30.305 | 30.278 | 30.249 | 30.215 | 30.025 | 29.883 | 29.756 | 29.59 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GRANGETOWN | 11 | 66 | Lackenby | LACKENBY | TS6 7AS | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GREATHAM | 11 | 132 | Greatham | SALTHOLME | TS25 2DD | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | Lackenby | LACKENBY | TS14 6GQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARLOW GREEN | 11 | 66 | West Boldon | WEST BOLDON | NE9 6NT | SP (DFES) | 14.4431 | 14.3281 | 14.2801 | 14.2311 | 14.1821 | 14.1221 | 14.0511 | 13.9711 | 13.8821 | 13.7791 | 13.2251 | 12.7291 | 12.2631 | 11.7811 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARMIRE BRIDGE | 20 | 66 | Toronto | SPENNYMOOR | DL12 8QJ | SP (DFES) | 8.313 | 8.129 | 8.086 | 8.043 | 7.999 | 7.95 | 7.891 | 7.832 | 7.769 | 7.692 | 7.246 | 6.976 | 6.721 | 6.371 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARRATON | 11 | 132 | Harraton | STELLA SOUTH | NE38 9BZ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.364 | 37.307 | 37.24 | 36.864 | 36.584 | 36.324 | 36.01 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/11KV | 11 | 132 | Harrogate 132/11kV | KNARESBOROUGH | HG1 2BN | SP (DFES) | 27.639 | 27.314 | 27.22 | 27.127 | 27.032 | 26.921 | 26.788 | 26.649 | 26.498 | 26.32 | 25.338 | 24.57 | 23.865 | 23.03 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE WEST | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 0QB | SP (DFES) | 32.573 | 32.47 | 32.445 | 32.42 | 32.394 | 32.365 | 32.33 | 32.294 | 32.256 | 32.21 | 31.956 | 31.775 | 31.611 | 31.398 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HARTMOOR 66/20KV | 20 | 66 | Hartmoor | HARTMOOR | TS27 3BL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HAWTHORN PIT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 9NX | SP (DFES) | 10.451 | 10.268 | 10.198 | 10.128 | 10.058 | 9.973 | 9.872 | 9.76 | 9.637 | 9.492 | 8.708 | 8.037 | 7.407 | 6.734 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | Melrosegate | OSBALDWICK | YO31 8FZ | SP (DFES) | 0.016716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN | 6 | 66 | West Boldon | WEST BOLDON | NE31 1BD | SP (DFES) | 0 | 4.8368 | 4.8258 | 4.8158 | 4.8058 | 4.7928 | 4.7788 | 4.7638 | 4.7488 | 4.7298 | 4.6258 | 4.5498 | 4.4808 | 4.3928 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN WEST | 11 | 66 | West Boldon | WEST BOLDON | NE31 1NA | SP (DFES) | 0.0046837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEDWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE32 4SW | SP (DFES) | 0.39029 | 0.32329 | 0.29529 | 0.26629 | 0.23729 | 0.20129 | 0.15929 | 0.11129 | 0.05929 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEIGHINGTON | 11 | 33 | Darlington North | NORTON | DL5 6JW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HEXHAM | 20 | 66 | Coalburns | STELLA SOUTH | NE46 4NT | SP (DFES) | 28.0099 | 27.8849 | 27.8479 | 27.8099 | 27.7719 | 27.7269 | 27.6729 | 27.6149 | 27.5519 | 27.4769 | 27.0589 | 26.7449 | 26.4489 | 26.1059 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HIGH BARMSTON | 11 | 66 | West Boldon | WEST BOLDON | NE38 8QA | SP (DFES) | 20.747 | 20.631 | 20.596 | 20.561 | 20.525 | 20.483 | 20.433 | 20.38 | 20.322 | 20.254 | 19.878 | 19.583 | 19.307 | 18.989 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HIGH FLATTS | 11 | 66 | Potter House | SPENNYMOOR | DH2 2LR | SP (DFES) | 21.3702 | 21.2292 | 21.1762 | 21.1232 | 21.0702 | 21.0052 | 20.9282 | 20.8442 | 20.7502 | 20.6402 | 20.0402 | 19.5352 | 19.0602 | 18.5492 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HOUGHTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | DH4 5HP | SP (DFES) | 3.8321 | 3.7131 | 3.6681 | 3.6231 | 3.5781 | 3.5231 | 3.4581 | 3.3871 | 3.3081 | 3.2151 | 2.7151 | 2.2841 | 1.8821 | 1.4501 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HOWDON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 0JX | SP (DFES) | 4.3505 | 4.3125 | 4.3005 | 4.2875 | 4.2755 | 4.2605 | 4.2425 | 4.2225 | 4.2015 | 4.1775 | 4.0455 | 3.9315 | 3.8275 | 3.7105 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUNTINGTON NEW LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO32 9TA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | Husthwaite | KNARESBOROUGH | YO61 4PN | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | JARROW | 11 | 33 | South Shields | SOUTH SHIELDS | NE32 5LD | SP (DFES) | 18.4166 | 18.3756 | 18.3646 | 18.3536 | 18.3426 | 18.3286 | 18.3136 | 18.2976 | 18.2806 | 18.2596 | 18.1466 | 18.0616 | 17.9826 | 17.8866 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KENTON | 11 | 33 | Blucher | STELLA NORTH | NE3 4UP | SP (DFES) | 3.2121 | 3.1251 | 3.0931 | 3.0601 | 3.0271 | 2.9871 | 2.9401 | 2.8881 | 2.8301 | 2.7641 | 2.4101 | 2.0881 | 1.7921 | 1.4761 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KIELDER | 20 | 33 | Spadeadam 33kV | SPADEADAM | NE48 1BH | SP (DFES) | 4.052 | 4.031 | 4.027 | 4.023 | 4.018 | 4.013 | 4.008 | 4.002 | 3.997 | 3.99 | 3.947 | 3.927 | 3.909 | 3.877 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KILLINGWORTH | 11 | 33 | Gosforth | TYNEMOUTH | NE12 6QQ | SP (DFES) | 11.602 | 11.523 | 11.493 | 11.464 | 11.433 | 11.397 | 11.354 | 11.306 | 11.254 | 11.193 | 10.868 | 10.575 | 10.305 | 10.016 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | KIRBYMOORSIDE | 11 | 66 | Malton Grid | OSBALDWICK | YO62 6EZ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LINTON 66/20KV | 20 | 66 | Linton | BLYTH 132kV | NE61 3AX | SP (DFES) | 7.384 | 7.298 | 7.267 | 7.237 | 7.206 | 7.169 | 7.124 | 7.076 | 7.022 | 6.958 | 6.61 | 6.325 | 6.057 | 5.766 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LONGBENTON | 11 | 33 | Gosforth | TYNEMOUTH | NE7 7LR | SP (DFES) | 19.5912 | 19.4902 | 19.4522 | 19.4142 | 19.3762 | 19.3292 | 19.2732 | 19.2122 | 19.1452 | 19.0682 | 18.6542 | 18.2782 | 17.9322 | 17.5632 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LOW SPENNYMOOR | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL16 7RS | SP (DFES) | 8.03 | 7.952 | 7.921 | 7.889 | 7.858 | 7.82 | 7.774 | 7.723 | 7.667 | 7.601 | 7.244 | 6.936 | 6.646 | 6.34 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | LYNEMOUTH | 20 | 66 | Linton | BLYTH 132kV | NE61 5XH | SP (DFES) | 6.08 | 6.063 | 6.056 | 6.048 | 6.041 | 6.032 | 6.021 | 6.009 | 5.995 | 5.979 | 5.894 | 5.819 | 5.748 | 5.675 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MADDISON STREET | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE24 1HD | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALLEABLE | 11 | 66 | North Tees | NORTON | TS18 2NR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0749 | 2.0229 | 1.9599 | 1.5959 | 1.3659 | 1.1499 | 0.85988 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MALTON | 11 | 66 | Malton Grid | OSBALDWICK | YO17 6BT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MEADOWFIELD | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH7 8ER | SP (DFES) | 0.896 | 0.827 | 0.808 | 0.789 | 0.771 | 0.749 | 0.723 | 0.696 | 0.667 | 0.632 | 0.434 | 0.298 | 0.169 | 0.009 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 33/11KV | 11 | 33 | Melrosegate | OSBALDWICK | YO31 0YB | SP (DFES) | 1.6717 | 1.5817 | 1.5547 | 1.5277 | 1.5007 | 1.4687 | 1.4307 | 1.3907 | 1.3477 | 1.2967 | 1.0237 | 0.7927 | 0.5847 | 0.3417 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MILLBANK LANE | 11 | 33 | Bowesfield | NORTON | TS17 0AX | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.8682 | 19.7912 | 19.7012 | 19.2212 | 18.7902 | 18.3862 | 17.9682 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MONKSEATON | 11 | 33 | Chirton Grange | TYNEMOUTH | NE25 9AF | SP (DFES) | 19.4432 | 19.2562 | 19.1962 | 19.1362 | 19.0752 | 19.0022 | 38.154 | 38.061 | 37.96 | 37.841 | 37.201 | 36.656 | 36.157 | 35.596 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MOOR MONKTON PUMPS | 11 | 33 | Poppleton | POPPLETON | YO30 1BY | SP (DFES) | 13.4099 | 13.3899 | 13.3839 | 13.3779 | 13.3719 | 13.3639 | 13.3559 | 13.3469 | 13.3369 | 13.3249 | 13.2609 | 13.2109 | 13.1639 | 13.1099 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MORPETH | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE61 6JH | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | MOUNT ROAD | 11 | 33 | Offerton | OFFERTON | SR4 7LJ | SP (DFES) | 24.0942 | 23.9162 | 23.8672 | 23.8162 | 23.7662 | 23.7062 | 23.6362 | 23.5622 | 23.4832 | 23.3882 | 22.8612 | 22.4662 | 22.0992 | 21.6572 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWBURN HAUGH | 11 | 132 | Newburn Haugh | STELLA NORTH | NE15 8SF | SP (DFES) | 20.4534 | 20.4094 | 20.3944 | 20.3804 | 20.3654 | 20.3474 | 20.3264 | 20.3044 | 20.2794 | 20.2514 | 20.0974 | 19.9634 | 19.8414 | 19.7054 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWBY | 11 | 33 | Scarborough Grid | OSBALDWICK | YO12 6NL | SP (DFES) | 0.22787 | 0.13587 | 0.098868 | 0.062868 | 0.025868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWCASTLE AIRPORT | 11 | 33 | Blucher | STELLA NORTH | NE13 8DF | SP (DFES) | 27.1463 | 27.0843 | 27.0573 | 27.0313 | 27.0043 | 26.9723 | 26.9333 | 26.8903 | 26.8423 | 26.7863 | 26.4853 | 26.2153 | 25.9633 | 25.7013 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | Darlington North | NORTON | DL5 6EA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH STREET | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 1DU | SP (DFES) | 1.3814 | 1.1384 | 1.0954 | 1.0524 | 1.0094 | 0.9614 | 0.9044 | 0.8534 | 0.8044 | 0.7454 | 0.4044 | 0.2004 | 0.041403 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T1 T2 | 11 | 66 | North Tees | NORTON | TS23 1PX | SP (DFES) | 22.3154 | 22.1694 | 22.1494 | 22.1294 | 22.1094 | 22.0884 | 22.0644 | 22.0454 | 22.0284 | 22.0054 | 21.8474 | 21.8374 | 21.8314 | 21.7254 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T3 T4 | 11 | 66 | North Tees | NORTON | TS23 1PY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8447 | 8.8047 | 8.7547 | 8.4627 | 8.3057 | 8.1597 | 7.9317 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTHALLERTON | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 0QE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | NORTON 132/11KV | 11 | 132 | Norton 132/11kV | NORTON | TS21 1EG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | OATLANDS | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 8BY | SP (DFES) | 18.3088 | 18.2078 | 18.1748 | 18.1408 | 18.1068 | 18.0668 | 18.0188 | 17.9668 | 17.9108 | 17.8438 | 17.4828 | 17.1808 | 16.9008 | 16.5898 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | OFFERTON 33/11KV | 11 | 33 | Offerton | OFFERTON | SR4 9NR | SP (DFES) | 26.6188 | 26.5198 | 26.4738 | 26.4288 | 26.3828 | 26.3258 | 26.2588 | 26.1838 | 26.0988 | 26.0008 | 25.4788 | 24.9988 | 24.5498 | 24.0908 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PALLION TRADING | 11 | 33 | Offerton | OFFERTON | SR4 6SN | SP (DFES) | 13.6178 | 13.4808 | 13.4398 | 13.3978 | 13.3558 | 13.3058 | 13.2468 | 13.1838 | 13.1158 | 13.0348 | 12.5898 | 12.2398 | 11.9148 | 11.5378 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2HR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE WEST | 11 | 66 | Hartmoor | HARTMOOR | DH6 2RA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PILGRIM | 11 | 33 | Barrack Road | STELLA NORTH | NE1 2LA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7362 | 3.7282 | 3.7162 | 3.6322 | 3.6372 | 3.6532 | 3.5892 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | Potter House | SPENNYMOOR | DH1 5FF | SP (DFES) | 4.547 | 4.409 | 4.353 | 4.295 | 4.238 | 4.168 | 4.084 | 3.991 | 3.887 | 3.766 | 3.112 | 2.538 | 2 | 1.437 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | Potter House | SPENNYMOOR | DH1 5FF | SP (DFES) | 26.2292 | 26.1882 | 26.1782 | 26.1682 | 26.1582 | 26.1462 | 26.1322 | 26.1182 | 26.1022 | 26.0842 | 25.9772 | 25.9082 | 25.8432 | 25.7592 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | PRISSICK | 11 | 66 | Lackenby | LACKENBY | TS4 3SG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSCAR | 11 | 33 | Scarborough Grid | OSBALDWICK | YO13 0LZ | SP (DFES) | 10.019 | 9.992 | 9.987 | 9.982 | 9.977 | 9.972 | 9.965 | 9.959 | 9.953 | 9.946 | 9.905 | 9.88 | 9.859 | 9.823 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RAWCLIFFE LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO30 5SW | SP (DFES) | 0.8637 | 0.7277 | 0.6887 | 0.6487 | 0.6087 | 0.5617 | 0.5057 | 0.4467 | 0.3837 | 0.3087 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | REDCAR | 11 | 66 | Lackenby | LACKENBY | TS10 2PA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RESERVOIR | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE22 5QP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T1 | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL10 5BJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T2 | 11 | 33 | Darlington North | NORTON | DL10 5BJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RIPON | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG4 1QE | SP (DFES) | 14.3879 | 14.1409 | 14.0769 | 17.971 | 17.907 | 17.832 | 17.744 | 17.654 | 17.557 | 17.442 | 16.795 | 16.331 | 15.904 | 15.364 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RISE CARR | 6 | 33 | Darlington North | NORTON | DL3 0RP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ROMANBY | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 8HP | SP (DFES) | 9.9921 | 9.9521 | 9.9291 | 9.9051 | 9.8821 | 9.8521 | 9.8171 | 9.7771 | 9.7311 | 9.6781 | 9.3961 | 9.1291 | 8.8781 | 8.6321 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | RUDBY | 11 | 33 | Bowesfield | NORTON | TS15 0JT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 2YH | SP (DFES) | 2.178 | 1.917 | 1.856 | 1.794 | 1.732 | 1.66 | 1.575 | 1.489 | 1.401 | 1.296 | 0.72502 | 0.27802 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEGHILL | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 7EY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | Husthwaite | KNARESBOROUGH | YO7 3NT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SEVERUS HILL | 11 | 33 | Poppleton | POPPLETON | YO26 4RR | SP (DFES) | 0.77757 | 0.65757 | 0.62157 | 0.58457 | 0.54857 | 0.50357 | 0.45157 | 0.39657 | 0.33757 | 0.26757 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SHERIFF HUTTON | 11 | 66 | Malton Grid | OSBALDWICK | YO60 6QN | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SHOTTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2EL | SP (DFES) | 1.3682 | 1.2652 | 1.2292 | 1.1922 | 1.1552 | 1.1112 | 1.0582 | 1.0012 | 0.93717 | 0.86217 | 0.45217 | 0.11517 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SIMONSIDE | 11 | 33 | South Shields | SOUTH SHIELDS | NE34 9PD | SP (DFES) | 13.2181 | 13.1371 | 13.1091 | 13.0801 | 13.0511 | 13.0161 | 12.9751 | 12.9291 | 12.8801 | 12.8221 | 12.5101 | 12.2391 | 11.9891 | 11.7161 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SKELDERGATE | 11 | 33 | Poppleton | POPPLETON | YO1 6HN | SP (DFES) | 2.0819 | 1.9169 | 1.8909 | 1.8639 | 1.8369 | 1.8069 | 1.7729 | 1.7429 | 1.7149 | 1.6789 | 1.4719 | 1.3739 | 1.2999 | 1.1249 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SKERNESIDE | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL5 6JH | SP (DFES) | 0.29662 | 0.13762 | 0.090618 | 0.043618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENCERBECK | 11 | 66 | Lackenby | LACKENBY | TS3 8TE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5JX | SP (DFES) | 0.73867 | 0.60067 | 0.55367 | 0.50667 | 0.45867 | 0.40067 | 0.33267 | 0.25867 | 0.17667 | 0.080669 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STARBECK | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 7PT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STOKESLEY | 11 | 33 | Bowesfield | NORTON | TS9 5HS | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | STONEY CUT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 8RQ | SP (DFES) | 15.8982 | 15.7762 | 15.7302 | 15.6842 | 15.6372 | 15.5822 | 15.5152 | 15.4412 | 15.3602 | 15.2642 | 14.7462 | 14.3072 | 13.8942 | 13.4522 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T1 T2 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | SP (DFES) | 21.0013 | 20.7793 | 20.7363 | 20.6923 | 20.6483 | 20.5993 | 20.5423 | 20.4863 | 20.4313 | 20.3613 | 19.9493 | 19.7373 | 19.5443 | 19.2233 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T5 T6 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | SP (DFES) | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TANFIELD | 11 | 66 | Annfield | STELLA SOUTH | DH9 9DB | SP (DFES) | 0.61315 | 0.50915 | 0.46715 | 0.42515 | 0.38215 | 0.33115 | 0.27015 | 0.20115 | 0.12515 | 0.03715 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEAM VALLEY | 20 | 66 | Ravensworth | STELLA SOUTH | NE11 0SX | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.2181 | 45.1951 | 45.1661 | 44.9761 | 44.9251 | 44.8791 | 44.7441 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | Seal Sands | SALTHOLME | TS23 3NF | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TEMPLE PARK | 11 | 66 | West Boldon | WEST BOLDON | NE34 8TH | SP (DFES) | 20.0994 | 19.9914 | 19.9454 | 19.8984 | 19.8514 | 19.7944 | 19.7254 | 19.6494 | 19.5644 | 19.4654 | 18.9404 | 18.4564 | 18.0064 | 17.5424 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | THIRSK | 11 | 33 | Leeming Bar_Skeeby | NORTON | YO7 4NH | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | THORNTON DALE | 11 | 66 | Malton Grid | OSBALDWICK | YO18 7SJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO 66/20KV | 20 | 66 | Toronto | SPENNYMOOR | DL14 7RJ | SP (DFES) | 8.158 | 7.959 | 7.902 | 7.844 | 7.786 | 7.717 | 7.636 | 7.549 | 7.455 | 7.344 | 6.717 | 6.256 | 5.821 | 5.307 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TUNSTALL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR3 2BT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.8669 | 26.7649 | 26.6469 | 26.0169 | 25.4409 | 24.9019 | 24.3479 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE30 1JG | SP (DFES) | 19.7015 | 19.4985 | 19.4465 | 19.3945 | 19.3415 | 19.2805 | 19.2075 | 19.1325 | 19.0535 | 18.9605 | 18.4425 | 18.0485 | 17.6935 | 17.2465 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | UNIVERSITY | 11 | 33 | Barrack Road | STELLA NORTH | NE2 4PZ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6497 | 10.6347 | 10.6147 | 10.5017 | 10.4417 | 10.3937 | 10.2977 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | URLAY NOOK | 11 | 33 | Bowesfield | NORTON | TS16 0QB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | USWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE37 3HY | SP (DFES) | 21.619 | 21.561 | 21.541 | 21.521 | 21.501 | 21.477 | 21.448 | 21.417 | 21.383 | 21.343 | 21.124 | 20.941 | 20.77 | 20.582 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WALKER | 11 | 66 | West Boldon | WEST BOLDON | NE6 3PZ | SP (DFES) | 14.6279 | 14.5009 | 14.4579 | 14.4149 | 14.3719 | 14.3199 | 14.2579 | 14.1919 | 14.1189 | 14.0349 | 13.5799 | 13.1829 | 12.8199 | 12.4179 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WANSBECK | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE22 7DH | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WARDLEY | 6 | 66 | West Boldon | WEST BOLDON | NE31 1LP | SP (DFES) | 0 | 15.7144 | 15.6914 | 15.6684 | 15.6444 | 15.6164 | 15.5824 | 15.5454 | 15.5034 | 15.4554 | 15.1954 | 14.9694 | 14.7584 | 14.5334 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WARKWORTH | 20 | 66 | Linton | BLYTH 132kV | NE65 0YD | SP (DFES) | 6.418 | 6.208 | 6.146 | 6.083 | 6.02 | 5.945 | 5.857 | 5.762 | 5.658 | 5.534 | 4.842 | 4.328 | 3.844 | 3.28 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WENSLEYDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5ED | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST HARTFORD | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 3JP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST SOUTHWICK | 11 | 66 | West Boldon | WEST BOLDON | SR5 3TX | SP (DFES) | 20.656 | 20.583 | 20.558 | 20.533 | 20.508 | 20.477 | 20.441 | 20.402 | 20.359 | 20.309 | 20.034 | 19.805 | 19.59 | 19.354 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WEST WYLAM | 20 | 66 | Coalburns | STELLA SOUTH | NE42 5EX | SP (DFES) | 0.22536 | 0.037363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WESTERHOPE | 11 | 33 | Blucher | STELLA NORTH | NE5 5HH | SP (DFES) | 19.0783 | 18.9993 | 18.9653 | 18.9303 | 18.8953 | 18.8533 | 18.8023 | 18.7463 | 18.6833 | 18.6113 | 18.2283 | 17.8673 | 17.5343 | 17.1903 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WESTOE | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 3GE | SP (DFES) | 13.182 | 13.072 | 13.034 | 12.996 | 12.958 | 12.911 | 12.856 | 12.797 | 12.731 | 12.654 | 12.241 | 11.885 | 11.556 | 11.196 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO22 4JE | SP (DFES) | 11.7831 | 11.7161 | 11.7031 | 11.6891 | 11.6761 | 11.6611 | 11.6431 | 11.6261 | 11.6091 | 11.5891 | 11.4761 | 11.3991 | 11.3361 | 11.2361 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO22 4JE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO21 1LY | SP (DFES) | 11.7099 | 11.6459 | 11.6309 | 11.6159 | 11.5999 | 11.5819 | 11.5609 | 11.5399 | 11.5179 | 11.4919 | 11.3499 | 11.2389 | 11.1419 | 11.0159 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO21 1LY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WILLINGTON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 7HS | SP (DFES) | 18.5692 | 18.4852 | 18.4482 | 18.4112 | 18.3742 | 18.3282 | 18.2742 | 18.2132 | 18.1452 | 18.0672 | 17.6522 | 17.2632 | 16.9032 | 16.5332 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | Wormald Green 132/11kV | KNARESBOROUGH | HG3 3PS | SP (DFES) | 13.141 | 13.035 | 13.006 | 12.977 | 12.948 | 12.913 | 12.872 | 12.829 | 12.783 | 12.728 | 12.425 | 12.195 | 11.983 | 11.727 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | WYNYARD | 11 | 66 | Hartmoor | HARTMOOR | TS2 2FB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | YEDINGHAM | 11 | 66 | Malton Grid | OSBALDWICK | YO17 8RR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | YORK UNIVERSITY | 11 | 33 | Melrosegate | OSBALDWICK | YO10 5ZF | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ABBEY ROAD | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS5 3NF | SP (DFES) | 1.8743 | 1.8543 | 1.8343 | 1.8133 | 1.7933 | 1.7673 | 1.7373 | 1.7013 | 1.6603 | 1.6133 | 1.3673 | 1.1113 | 0.86533 | 0.63333 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AIREDALE ROAD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 4LJ | SP (DFES) | 13.0876 | 13.0726 | 13.0576 | 13.0426 | 13.0276 | 13.0086 | 12.9856 | 12.9586 | 12.9286 | 12.8936 | 12.7116 | 12.5196 | 12.3366 | 12.1636 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALDHAM | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S73 8SW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALFRED GELDER STREET | 11 | 33 | Hull South | CREYKE BECK | HU1 1EP | SP (DFES) | 2.8809 | 2.8729 | 2.8649 | 2.8569 | 2.8489 | 2.8379 | 2.8259 | 2.8109 | 2.7949 | 2.7759 | 2.6779 | 2.5739 | 2.4739 | 2.3799 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T1 | 11 | 33 | Leeds East | SKELTON GRANGE | LS7 3QB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T2 | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 3QB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ALVERTHORPE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 9PB | SP (DFES) | 21.7093 | 21.6713 | 21.6353 | 21.5983 | 21.5613 | 21.5153 | 21.4603 | 21.3963 | 21.3213 | 21.2353 | 20.7793 | 20.3263 | 19.8853 | 19.4693 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARMOURIES DRIVE | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LT | SP (DFES) | 7.118 | 7.109 | 7.099 | 7.09 | 7.08 | 7.068 | 7.054 | 7.037 | 7.018 | 6.996 | 6.881 | 6.762 | 6.646 | 6.538 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARMTHORPE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3DY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ARUNDEL STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4PJ | SP (DFES) | 4.4368 | 4.4318 | 4.4268 | 4.4218 | 4.4168 | 4.4098 | 4.4018 | 4.3928 | 4.3828 | 4.3708 | 4.3088 | 4.2428 | 4.1798 | 4.1208 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ASKERN | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN6 0BY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AUDBY LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 7SU | SP (DFES) | 3.5894 | 3.5604 | 3.5324 | 3.5054 | 3.4784 | 3.4444 | 3.4044 | 3.3564 | 3.3004 | 3.2354 | 2.8814 | 2.5584 | 2.2344 | 1.9294 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | AUSTERFIELD | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN10 6HD | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BAILIFF BRIDGE | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 4DT | SP (DFES) | 1.3155 | 1.2945 | 1.2735 | 1.2515 | 1.2305 | 1.2045 | 1.1735 | 1.1365 | 1.0935 | 1.0455 | 0.79448 | 0.52848 | 0.27448 | 0.035483 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BALBY | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN4 8DG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BALME STREET | 11 | 33 | Bradford | BRADFORD WEST | BD1 4BA | SP (DFES) | 3.3296 | 3.3156 | 3.3006 | 3.2856 | 3.2696 | 3.2516 | 3.2286 | 3.2026 | 3.1726 | 3.1376 | 2.9586 | 2.7686 | 2.5866 | 2.4156 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNBURGH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 9NT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNOLDSWICK | 11 | 33 | Silsden | BRADFORD WEST | BB18 5RU | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 7AU | SP (DFES) | 32.1682 | 32.1542 | 32.1392 | 32.1242 | 32.1092 | 32.0912 | 32.0692 | 32.0432 | 32.0132 | 31.9792 | 31.8032 | 31.6162 | 31.4372 | 31.2682 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARROW | 11 | 33 | Immingham | GRIMSBY WEST | DN19 7EG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 66/11KV | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1HT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BARWICK | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS15 8SW | SP (DFES) | 13.1284 | 13.1024 | 13.0754 | 13.0484 | 13.0214 | 12.9874 | 12.9474 | 12.9004 | 12.8464 | 12.7844 | 12.4614 | 12.1234 | 11.7994 | 11.4934 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BASLOW ROAD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S17 3LT | SP (DFES) | 0.24192 | 0.21992 | 0.19792 | 0.17492 | 0.15192 | 0.12392 | 0.089919 | 0.050919 | 0.0049191 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BATLEY | 11 | 33 | Thornhill 132kV | ELLAND | WF17 6HU | SP (DFES) | 4.8824 | 4.8454 | 4.8084 | 4.7714 | 4.7344 | 4.6884 | 4.6334 | 4.5694 | 4.4944 | 4.4104 | 3.9674 | 3.5034 | 3.0584 | 2.6394 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEAL | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8DT | SP (DFES) | 3.9231 | 3.9061 | 3.8901 | 3.8741 | 3.8591 | 3.8401 | 3.8171 | 3.7901 | 3.7581 | 3.7211 | 3.5211 | 3.3351 | 3.1511 | 2.9771 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | SP (DFES) | 8.5795 | 8.5715 | 8.5635 | 8.5555 | 8.5475 | 8.5375 | 8.5255 | 8.5115 | 8.4955 | 8.4765 | 8.3795 | 8.2795 | 8.1825 | 8.0905 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | SP (DFES) | 38.4382 | 38.4192 | 38.4002 | 38.3812 | 38.3622 | 38.3382 | 38.3102 | 38.2762 | 38.2382 | 38.1942 | 37.9652 | 37.7272 | 37.4972 | 37.2812 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BEIGHTON | 11 | 66 | Thurcroft | THURCROFT | S26 4TL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELLHOUSE ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 0PL | SP (DFES) | 1.3507 | 1.3147 | 1.2777 | 1.2417 | 1.2047 | 1.1597 | 1.1047 | 1.0407 | 0.96773 | 0.88473 | 0.44973 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT AVENUE | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DF | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT COVERT | 11 | 33 | Wold Newton | KEADBY | LN11 9RA | SP (DFES) | 0.029462 | 0.026462 | 0.023462 | 0.021462 | 0.019462 | 0.016462 | 0.013462 | 0.0094624 | 0.0054624 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BELTHORPE LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1SB | SP (DFES) | 12.343 | 12.337 | 12.332 | 12.327 | 12.322 | 12.316 | 12.309 | 12.301 | 12.29 | 12.279 | 12.214 | 12.156 | 12.097 | 12.043 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BENTLEY | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN5 0NG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BILLET LANE | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINBROOK | 11 | 33 | Wold Newton | KEADBY | LN8 6DR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 33/11KV | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | SP (DFES) | 13.4226 | 13.3956 | 13.3686 | 13.3406 | 13.3126 | 13.2786 | 13.2376 | 13.1896 | 13.1346 | 13.0716 | 12.7436 | 12.3976 | 12.0656 | 11.7536 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BIRKBY | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 5HB | SP (DFES) | 0.29955 | 0.27155 | 0.24355 | 0.21555 | 0.18655 | 0.15155 | 0.10955 | 0.059548 | 0.0025485 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1HF | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BLUE BOY STREET | 11 | 33 | Neepsend | NEEPSEND | S3 7BA | SP (DFES) | 1.364 | 1.358 | 1.352 | 1.347 | 1.341 | 1.334 | 1.325 | 1.315 | 1.304 | 1.291 | 1.223 | 1.152 | 1.083 | 1.018 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOC BRINSWORTH | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1WT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOLTON ROAD | 11 | 33 | Silsden | BRADFORD WEST | BD20 0JT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BOTTESFORD | 11 | 33 | Scunthorpe South | KEADBY | DN16 3UJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHOPE | 11 | 33 | Menston | BRADFORD WEST | LS16 9HA | SP (DFES) | 0.75611 | 0.75011 | 0.74311 | 0.73611 | 0.73011 | 0.72111 | 0.71111 | 0.70011 | 0.68611 | 0.67111 | 0.59011 | 0.50611 | 0.42611 | 0.35011 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRAMLEY | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS13 3ST | SP (DFES) | 21.6578 | 21.6208 | 21.5838 | 21.5468 | 21.5098 | 21.4638 | 21.4078 | 21.3428 | 21.2678 | 21.1828 | 20.7358 | 20.2688 | 19.8198 | 19.3978 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRETT STREET | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 4HW | SP (DFES) | 17.2185 | 17.1495 | 17.0845 | 17.0185 | 16.9565 | 16.8805 | 16.7895 | 16.6785 | 16.5495 | 16.4005 | 15.5905 | 14.8345 | 14.0895 | 13.3905 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIDGES ROAD | 11 | 33 | Scunthorpe South | KEADBY | DN17 1HA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1QE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BRODSWORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 7XB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BROOKFIELD STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LD | SP (DFES) | 2.5369 | 2.5359 | 2.5349 | 2.5339 | 2.5329 | 2.5319 | 2.5309 | 2.5289 | 2.5269 | 2.5249 | 2.5129 | 2.5009 | 2.4889 | 2.4779 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BTP | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN31 2RL | SP (DFES) | 16.3847 | 16.3847 | 16.3847 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3827 | 16.3827 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURLEY STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS3 1JY | SP (DFES) | 40.0041 | 39.9931 | 39.9831 | 39.9721 | 39.9611 | 39.9481 | 39.9321 | 39.9131 | 39.8921 | 39.8671 | 39.7391 | 39.6051 | 39.4771 | 39.3551 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURMANTOFTS | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 7SS | SP (DFES) | 10.3215 | 10.3135 | 10.3055 | 10.2965 | 10.2885 | 10.2775 | 10.2655 | 10.2505 | 10.2335 | 10.2135 | 10.1125 | 10.0065 | 9.9045 | 9.8085 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURNLEYVILLE | 11 | 33 | Heckmondwike | SKELTON GRANGE | BD19 4RY | SP (DFES) | 1.8974 | 1.8694 | 1.8404 | 1.8114 | 1.7824 | 1.7464 | 1.7034 | 1.6524 | 1.5944 | 1.5274 | 1.1814 | 0.8174 | 0.4684 | 0.1404 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURTON PIDSEA | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU12 9AE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BURTON ROAD | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 2QG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 2HG | SP (DFES) | 10.8333 | 10.8073 | 10.7813 | 10.7543 | 10.7283 | 10.6953 | 10.6563 | 10.6103 | 10.5573 | 10.4963 | 10.1803 | 9.8493 | 9.5323 | 9.2333 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | BUTTERWICK | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO17 8HF | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CAISTOR | 11 | 33 | Wold Newton | KEADBY | LN7 6RE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CALDER WHARF | 11 | 33 | Thornhill 132kV | ELLAND | WF13 3JQ | SP (DFES) | 19.9288 | 19.8978 | 19.8668 | 19.8358 | 19.8048 | 19.7668 | 19.7198 | 19.6658 | 19.6028 | 19.5318 | 19.1598 | 18.7698 | 18.3958 | 18.0438 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CARLTON HILL | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 1JB | SP (DFES) | 22.2214 | 22.2094 | 22.1984 | 22.1864 | 22.1744 | 22.1604 | 22.1434 | 22.1224 | 22.0994 | 22.0734 | 21.9334 | 21.7884 | 21.6494 | 21.5174 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CARR LANE | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 4PS | SP (DFES) | 22.4807 | 22.4557 | 22.4317 | 22.4067 | 22.3817 | 22.3517 | 22.3157 | 22.2727 | 22.2227 | 22.1657 | 21.8617 | 21.5607 | 21.2677 | 20.9907 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CHELKER RESERVOIR | 11 | 33 | Silsden | BRADFORD WEST | LS29 0JS | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CHEVIN END | 11 | 33 | Menston | BRADFORD WEST | LS29 6BE | SP (DFES) | 23.4265 | 23.4085 | 23.3905 | 23.3725 | 23.3545 | 23.3315 | 23.3045 | 23.2725 | 23.2365 | 23.1945 | 22.9775 | 22.7475 | 22.5285 | 22.3215 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENCE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1JE | SP (DFES) | 7.64 | 7.633 | 7.627 | 7.62 | 7.614 | 7.606 | 7.596 | 7.585 | 7.571 | 7.556 | 7.478 | 7.396 | 7.318 | 7.244 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON ROAD | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS2 9JT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON STREET | 11 | 33 | Hull South | CREYKE BECK | HU3 1AP | SP (DFES) | 22.2899 | 22.2749 | 22.2599 | 22.2449 | 22.2299 | 22.2109 | 22.1879 | 22.1619 | 22.1309 | 22.0969 | 21.9169 | 21.7259 | 21.5429 | 21.3699 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLAYWHEELS LANE | 11 | 33 | Neepsend | NEEPSEND | S6 1LY | SP (DFES) | 22.6721 | 22.6251 | 22.5781 | 22.5301 | 22.4821 | 22.4221 | 22.3511 | 22.2671 | 22.1701 | 22.0611 | 21.4911 | 20.8861 | 20.3081 | 19.7641 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CLOUGH LANE | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3EH | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COMMONSIDE LANE | 11 | 33 | Featherstone | FERRYBRIDGE B | WF7 5DF | SP (DFES) | 5.3768 | 5.3548 | 5.3328 | 6.0108 | 5.9888 | 5.9618 | 5.9298 | 5.8908 | 5.8468 | 5.7958 | 5.5238 | 5.2548 | 4.9918 | 4.7438 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CONVAMORE ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN32 9PG | SP (DFES) | 14.0823 | 14.0573 | 14.0333 | 14.0083 | 13.9833 | 13.9523 | 13.9163 | 13.8723 | 13.8223 | 13.7643 | 13.4603 | 13.1533 | 12.8563 | 12.5753 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CONYARD ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN35 7LQ | SP (DFES) | 10.7616 | 10.7276 | 10.6946 | 10.6616 | 10.6286 | 10.5876 | 10.5386 | 10.4806 | 10.4136 | 10.3376 | 9.9316 | 9.5226 | 9.1256 | 8.7516 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CORNWALL STREET | 11 | 132 | Cornwall Street | CREYKE BECK | HU8 8AQ | SP (DFES) | 32.4477 | 32.4327 | 32.4187 | 32.4037 | 32.3897 | 32.3707 | 32.3487 | 32.3237 | 32.2937 | 32.2607 | 32.0867 | 31.9017 | 31.7247 | 31.5587 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CORRINGHAM ROAD | 11 | 33 | Blyton | KEADBY | DN21 1FT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COSTHORPE | 11 | 66 | Thurcroft | THURCROFT | S81 9QR | SP (DFES) | 6.6821 | 6.6691 | 6.6571 | 6.6451 | 6.6341 | 6.6211 | 6.6041 | 6.5841 | 6.5601 | 6.5321 | 6.3731 | 6.2461 | 6.1131 | 5.9881 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | COUNTY ROAD NORTH | 11 | 33 | Hull South | CREYKE BECK | HU5 5DR | SP (DFES) | 8.3364 | 8.2824 | 8.2284 | 8.1734 | 8.1194 | 8.0524 | 7.9724 | 7.8784 | 7.7694 | 7.6444 | 6.9864 | 6.3164 | 5.6684 | 5.0584 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CRACOE | 11 | 33 | Silsden | BRADFORD WEST | BD23 6BE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROOKESMOOR ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 3FP | SP (DFES) | 3.6007 | 3.5627 | 3.5247 | 3.4867 | 3.4477 | 3.3997 | 3.3427 | 3.2757 | 3.1977 | 3.1107 | 2.6527 | 2.1677 | 1.7047 | 1.2677 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROSSHILLS | 11 | 33 | Silsden | BRADFORD WEST | BD20 7AQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROWLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN17 4BB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | CROWN STREET | 11 | 33 | Girlington | BRADFORD WEST | BD1 2LA | SP (DFES) | 0.78571 | 0.78171 | 0.77671 | 0.77271 | 0.76871 | 0.76371 | 0.75771 | 0.74971 | 0.74171 | 0.73171 | 0.68271 | 0.62971 | 0.57971 | 0.53271 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DALTON | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD2 1FF | SP (DFES) | 2.736 | 2.694 | 2.653 | 2.611 | 2.569 | 2.517 | 2.455 | 2.382 | 2.298 | 2.202 | 1.702 | 1.177 | 0.674 | 0.2 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DARNALL | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 4JT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DEARNE ROAD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DEIGHTON | 11 | 33 | Brighouse 132/33kV | ELLAND | HD2 1UP | SP (DFES) | 18.468 | 18.444 | 18.42 | 18.396 | 18.372 | 18.343 | 18.307 | 18.265 | 18.217 | 18.162 | 17.876 | 17.576 | 17.288 | 17.017 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENBY DALE ROAD | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7BH | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENBY GRANGE | 11 | 33 | Thornhill 132kV | ELLAND | WF4 4JG | SP (DFES) | 0.32811 | 0.32011 | 0.31211 | 0.30411 | 0.29611 | 0.28611 | 0.27411 | 0.26011 | 0.24311 | 0.22411 | 0.12511 | 0.02511 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DENHOLME | 11 | 33 | Holmfield | BRADFORD WEST | BD13 4JF | SP (DFES) | 11.6087 | 11.5997 | 11.5917 | 11.5827 | 11.5747 | 11.5637 | 11.5507 | 11.5357 | 11.5177 | 11.4987 | 11.3957 | 11.2867 | 11.1827 | 11.0847 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DINNINGTON | 11 | 66 | Thurcroft | THURCROFT | S25 3QT | SP (DFES) | 0 | 22.4707 | 22.4377 | 22.4047 | 22.3727 | 22.3317 | 22.2837 | 22.2257 | 22.1597 | 22.0837 | 21.6807 | 21.2787 | 20.8867 | 20.5167 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DOUGHTY ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN32 0LR | SP (DFES) | 3.9288 | 3.8818 | 3.8358 | 3.7888 | 3.7418 | 3.6848 | 3.6148 | 3.5328 | 3.4388 | 3.3308 | 2.7578 | 2.1808 | 1.6208 | 1.0938 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DOWKER STREET | 11 | 33 | Lindley | ELLAND | HD3 4JB | SP (DFES) | 0.53351 | 0.51151 | 0.48951 | 0.46751 | 0.44551 | 0.41851 | 0.38551 | 0.34751 | 0.30351 | 0.25351 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRAX PRIMARY | 11 | 66 | Camblesforth | CAMBLESFORTH | YO8 6PQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 5XR | SP (DFES) | 13.9655 | 13.8975 | 13.8325 | 13.7675 | 13.7065 | 13.6315 | 13.5415 | 13.4325 | 13.3045 | 13.1575 | 12.3575 | 11.6135 | 10.8775 | 10.1865 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DRONFIELD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S18 2XU | SP (DFES) | 1.7102 | 1.6932 | 1.6772 | 1.6602 | 1.6432 | 1.6232 | 1.5982 | 1.5692 | 1.5362 | 1.4982 | 1.2972 | 1.0902 | 0.8912 | 0.7042 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DUDLEY HILL | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9NW | SP (DFES) | 23.1778 | 23.1608 | 23.1438 | 23.1268 | 23.1088 | 23.0878 | 23.0618 | 23.0318 | 22.9978 | 22.9588 | 22.7538 | 22.5378 | 22.3308 | 22.1358 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DUNKESWICK | 11 | 33 | Bramham | FERRYBRIDGE B | LS17 9LP | SP (DFES) | 12.0853 | 12.0663 | 12.0503 | 12.0333 | 12.0183 | 12.0003 | 11.9783 | 11.9503 | 11.9163 | 11.8743 | 11.6273 | 11.4703 | 11.2933 | 11.1243 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | DURKAR LOW LANE | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF4 3BJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EASINGTON | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0SU | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EASTFIELD ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ECCLESFIELD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 9YR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EDLINGTON | 11 | 66 | Thurcroft | THURCROFT | DN12 1SU | SP (DFES) | 13.6335 | 13.5935 | 13.5545 | 13.5155 | 13.4765 | 13.4295 | 13.3715 | 13.3035 | 13.2255 | 13.1355 | 12.6575 | 12.1795 | 11.7155 | 11.2785 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EGGBOROUGH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | DN14 0QA | SP (DFES) | 7.4436 | 7.4356 | 7.4286 | 7.4216 | 7.4146 | 7.4066 | 7.3966 | 7.3836 | 7.3696 | 7.3536 | 7.2636 | 7.1806 | 7.0996 | 7.0226 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELGAR ROAD | 11 | 33 | Hull West | CREYKE BECK | HU4 7NY | SP (DFES) | 22.0527 | 21.9967 | 21.9427 | 21.8877 | 21.8357 | 21.7717 | 21.6937 | 21.6007 | 21.4927 | 21.3687 | 20.7007 | 20.0557 | 19.4247 | 18.8327 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLAND 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX5 9AE | SP (DFES) | 20.0125 | 19.9925 | 19.9715 | 19.9505 | 19.9295 | 19.9045 | 19.8735 | 19.8375 | 19.7955 | 19.7485 | 19.5015 | 19.2405 | 18.9915 | 18.7565 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIFOOT LANE | 11 | 33 | Saltend 132/33kV | SALTEND NORTH | HU12 9EB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 1/3 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | SP (DFES) | 4.8208 | 4.8058 | 4.7908 | 4.7758 | 4.7598 | 4.7408 | 4.7178 | 4.6918 | 4.6608 | 4.6258 | 4.4428 | 4.2498 | 4.0648 | 3.8908 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 2 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 1 | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 4LS | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 2 | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S75 4LS | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ELSECAR | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S74 8AU | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ENDIKE LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 8AY | SP (DFES) | 16.5674 | 16.5334 | 16.5004 | 16.4664 | 16.4334 | 16.3924 | 16.3434 | 16.2844 | 16.2174 | 16.1404 | 15.7324 | 15.3204 | 14.9214 | 14.5464 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | EPWORTH | 11 | 33 | Blyton | KEADBY | DN9 1JU | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FARNLEY CRESCENT | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 5AN | SP (DFES) | 0.87808 | 0.84808 | 0.81908 | 0.78908 | 0.76008 | 0.72308 | 0.67908 | 0.62708 | 0.56708 | 0.50008 | 0.14408 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FENTON LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6EZ | SP (DFES) | 5.1162 | 5.1042 | 5.0932 | 5.0822 | 5.0722 | 5.0592 | 5.0442 | 5.0262 | 5.0042 | 4.9792 | 4.8422 | 4.7172 | 4.5932 | 4.4772 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF11 8RR | SP (DFES) | 2.244 | 2.188 | 2.133 | 2.078 | 2.024 | 1.957 | 1.877 | 1.781 | 1.67 | 1.543 | 0.862 | 0.198 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIR TREE LANE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS17 7BZ | SP (DFES) | 3.9108 | 3.8738 | 3.8368 | 3.7988 | 3.7618 | 3.7158 | 3.6598 | 3.5948 | 3.5198 | 3.4338 | 2.9858 | 2.5188 | 2.0698 | 1.6468 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIRST AVENUE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 9NE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FIRTH BROWN | 11 | 33 | Santon | KEADBY | DN16 1XP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FISH DAM LANE | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 3HQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FLIXBOROUGH | 11 | 33 | Scunthorpe North | KEADBY | DN15 8RR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOLLY HALL | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 3TF | SP (DFES) | 1.8277 | 1.8097 | 1.7927 | 1.7747 | 1.7567 | 1.7347 | 1.7077 | 1.6767 | 1.6407 | 1.5997 | 1.3867 | 1.1627 | 0.9477 | 0.7457 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOUR LANE ENDS | 11 | 33 | Girlington | BRADFORD WEST | BD8 0LJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FOXHILLS | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FULLERTON ROAD | 11 | 33 | Templeborough 275/33KV | TEMPLEBOROUGH 275/33KV | S60 1DL | SP (DFES) | 0.12587 | 0.11287 | 0.09987 | 0.08687 | 0.07387 | 0.05787 | 0.03887 | 0.01587 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | FURNESS AVENUE | 11 | 33 | Holmfield | BRADFORD WEST | WF8 3JA | SP (DFES) | 1.1729 | 1.1409 | 1.1089 | 1.0759 | 1.0439 | 1.0039 | 0.95586 | 0.89986 | 0.83486 | 0.76086 | 0.37786 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GAISBY LANE | 11 | 33 | Bradford | BRADFORD WEST | BD2 1BB | SP (DFES) | 3.163 | 3.133 | 3.102 | 3.071 | 3.04 | 3.002 | 2.956 | 2.902 | 2.84 | 2.769 | 2.402 | 2.013 | 1.641 | 1.291 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIBRALTAR ROAD | 11 | 33 | Holmfield | BRADFORD WEST | HX1 4HL | SP (DFES) | 4.3791 | 4.3351 | 4.2901 | 4.2451 | 4.2011 | 4.1461 | 4.0801 | 4.0021 | 3.9131 | 3.8111 | 3.2831 | 2.7221 | 2.1861 | 1.6831 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GIBSON LANE | 11 | 33 | Hull West | CREYKE BECK | HU14 3HH | SP (DFES) | 17.154 | 17.103 | 17.054 | 17.005 | 16.959 | 16.903 | 16.835 | 16.753 | 16.656 | 16.545 | 15.943 | 15.381 | 14.827 | 14.307 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GILDERSOME | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 7HW | SP (DFES) | 0.67587 | 0.65987 | 0.64287 | 0.62587 | 0.60887 | 0.58787 | 0.56287 | 0.53387 | 0.49987 | 0.46087 | 0.25887 | 0.046867 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GLEADLESS VALLEY | 11 | 33 | Norton Lees | NORTON LEES | S14 1FP | SP (DFES) | 1.808 | 1.776 | 1.745 | 1.713 | 1.681 | 1.641 | 1.594 | 1.538 | 1.474 | 1.401 | 1.022 | 0.61998 | 0.23498 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GOOLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 6SX | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GRAINTHORPE | 11 | 33 | Wold Newton | KEADBY | LN11 7JU | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREAT COATES | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN37 9PN | SP (DFES) | 2.2171 | 2.1811 | 2.1451 | 2.1091 | 2.0731 | 2.0281 | 1.9751 | 1.9111 | 1.8381 | 1.7541 | 1.3071 | 0.86509 | 0.43309 | 0.027087 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREENHILL | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 7RJ | SP (DFES) | 0.89023 | 0.87123 | 0.85323 | 0.83423 | 0.81523 | 0.79123 | 0.76323 | 0.73023 | 0.69223 | 0.64923 | 0.42323 | 0.18523 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS RD | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GRIMETHORPE | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S72 7BQ | SP (DFES) | 15.5699 | 15.5529 | 15.5359 | 15.5189 | 15.5019 | 15.4809 | 15.4559 | 15.4259 | 15.3919 | 15.3529 | 15.1439 | 14.9359 | 14.7329 | 14.5419 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GROVE STREET | 11 | 33 | Lindley | ELLAND | HD1 2PB | SP (DFES) | 13.6852 | 13.6792 | 13.6732 | 13.6672 | 13.6602 | 13.6532 | 13.6442 | 13.6332 | 13.6212 | 13.6072 | 13.5352 | 13.4592 | 13.3862 | 13.3172 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | GUARDIAN GLASS | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8GA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HACKENTHORPE | 11 | 66 | Thurcroft | THURCROFT | S12 4ET | SP (DFES) | 24.2556 | 24.2236 | 24.1916 | 24.1586 | 24.1266 | 24.0866 | 24.0386 | 23.9816 | 23.9166 | 23.8426 | 23.4586 | 23.0516 | 22.6616 | 22.2946 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 33/11KV | 11 | 33 | Halifax 132/33kV | ELLAND | HX1 1XB | SP (DFES) | 2.4426 | 2.4136 | 2.3846 | 2.3546 | 2.3256 | 2.2896 | 2.2456 | 2.1946 | 2.1366 | 2.0696 | 1.7216 | 1.3536 | 1.0016 | 0.67062 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HALLAM STREET | 11 | 33 | Menston | BRADFORD WEST | LS20 8AG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARDEN | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 1BG | SP (DFES) | 6.1463 | 6.1373 | 6.1283 | 6.1193 | 6.1103 | 6.0983 | 6.0843 | 6.0683 | 6.0503 | 6.0293 | 5.9183 | 5.8023 | 5.6913 | 5.5863 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARPSWELL | 11 | 33 | Blyton | KEADBY | DN21 5UT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HARWORTH | 11 | 66 | Thurcroft | THURCROFT | DN11 8JW | SP (DFES) | 19.5975 | 19.5815 | 19.5665 | 19.5515 | 19.5365 | 19.5185 | 19.4965 | 19.4705 | 19.4405 | 19.4045 | 19.2085 | 19.0335 | 18.8575 | 18.6925 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 1 | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD22 9EP | SP (DFES) | 13.6866 | 13.6726 | 13.6586 | 13.6446 | 13.6306 | 13.6126 | 13.5916 | 13.5676 | 13.5386 | 13.5066 | 13.3386 | 13.1606 | 12.9906 | 12.8306 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 2 | 11 | 33 | Silsden | BRADFORD WEST | BD22 9EP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAXEY | 11 | 33 | Blyton | KEADBY | DN9 2LT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAYTON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1RJ | SP (DFES) | 0 | 0 | 0 | 16.4395 | 16.4065 | 16.3655 | 16.3165 | 16.2565 | 16.1865 | 16.1055 | 15.6675 | 15.2605 | 14.8575 | 14.4795 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HAZLEHEAD | 11 | 33 | Thornhill 132kV | ELLAND | S36 4HG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEBDEN BRIDGE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 6LX | SP (DFES) | 7.5017 | 7.4927 | 7.4837 | 7.4747 | 7.4657 | 7.4547 | 7.4417 | 7.4257 | 7.4077 | 7.3877 | 7.2807 | 7.1687 | 7.0607 | 6.9597 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEDLEY CHASE | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 1YN | SP (DFES) | 12.7018 | 12.6948 | 12.6878 | 12.6808 | 12.6738 | 12.6648 | 12.6538 | 12.6418 | 12.6278 | 12.6108 | 12.5258 | 12.4368 | 12.3508 | 12.2698 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEDON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 8ED | SP (DFES) | 11.4125 | 11.4105 | 11.4085 | 11.4065 | 11.4035 | 11.4015 | 11.3975 | 11.3935 | 11.3895 | 11.3845 | 11.3575 | 11.3295 | 11.3025 | 11.2765 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HEMSWORTH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 5BZ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 1 | 11 | 33 | Hull South | CREYKE BECK | HU4 6SP | SP (DFES) | 0.88484 | 0.87184 | 0.85884 | 0.84584 | 0.83284 | 0.81784 | 0.79884 | 0.77684 | 0.75084 | 0.72084 | 0.56184 | 0.40684 | 0.25584 | 0.11384 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 2 | 11 | 33 | Hull West | CREYKE BECK | HU4 6SP | SP (DFES) | 1.5085 | 1.4965 | 1.4835 | 1.4715 | 1.4585 | 1.4445 | 1.4265 | 1.4045 | 1.3795 | 1.3515 | 1.1995 | 1.0495 | 0.90452 | 0.76752 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HIBALDSTOW | 11 | 33 | Santon | KEADBY | DN21 4NH | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HICKLETON | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 0DE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HILLCREST | 11 | 33 | Leeds East | SKELTON GRANGE | LS8 3AA | SP (DFES) | 3.5459 | 3.5109 | 3.4759 | 3.4399 | 3.4039 | 3.3599 | 3.3069 | 3.2439 | 3.1719 | 3.0899 | 2.6619 | 2.2149 | 1.7849 | 1.3799 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLBECK | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9SZ | SP (DFES) | 4.083 | 4.056 | 4.029 | 4.001 | 3.974 | 3.94 | 3.899 | 3.852 | 3.796 | 3.734 | 3.406 | 3.064 | 2.735 | 2.425 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLDERNESS | 11 | 33 | Bransholme | CREYKE BECK | HU9 4AU | SP (DFES) | 0.18851 | 0.14051 | 0.093508 | 0.046508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 4BX | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 20.7205 | 20.7005 | 20.6765 | 20.6475 | 20.6155 | 20.4365 | 20.2725 | 20.1095 | 19.9565 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HONLEY | 11 | 33 | Lindley | ELLAND | HD9 6RU | SP (DFES) | 10.4499 | 10.4209 | 10.3919 | 10.3629 | 10.3339 | 10.2969 | 10.2539 | 10.2029 | 10.1439 | 10.0779 | 9.7279 | 9.3619 | 9.0109 | 8.6799 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOPE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S33 6RP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HORBURY | 11 | 33 | Thornhill 132kV | ELLAND | WF4 6EU | SP (DFES) | 18.0003 | 17.9703 | 17.9403 | 17.9103 | 17.8813 | 17.8443 | 17.8003 | 17.7483 | 17.6883 | 17.6193 | 17.2513 | 16.8863 | 16.5303 | 16.1953 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HOUGHTON MAIN | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S72 0GX | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 33/11KV | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5NP | SP (DFES) | 22.7896 | 22.7486 | 22.7086 | 22.6686 | 22.6306 | 22.5846 | 22.5286 | 22.4606 | 22.3826 | 22.2916 | 21.8016 | 21.3376 | 20.8816 | 20.4536 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUMBER ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LZ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | HUNMANBY | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO14 0JY | SP (DFES) | 20.2935 | 20.2635 | 20.2385 | 20.2135 | 20.1905 | 20.1635 | 20.1295 | 20.0875 | 20.0355 | 19.9735 | 19.6065 | 19.3625 | 19.0915 | 18.8355 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ICI FIBRES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4LT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IDLE | 11 | 33 | Bradford | BRADFORD WEST | BD10 8SA | SP (DFES) | 2.6811 | 2.6481 | 2.6151 | 2.5821 | 2.5481 | 2.5071 | 2.4571 | 2.3981 | 2.3311 | 2.2551 | 1.8561 | 1.4351 | 1.0321 | 0.65205 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ILKLEY | 11 | 33 | Silsden | BRADFORD WEST | LS29 9BE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | INGS LANE | 11 | 33 | Silsden | BRADFORD WEST | BD23 1UP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | IVESON HOUSE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 6RF | SP (DFES) | 20.9146 | 20.8816 | 20.8486 | 20.8146 | 20.7806 | 20.7396 | 20.6896 | 20.6306 | 20.5626 | 20.4856 | 20.0816 | 19.6596 | 19.2546 | 18.8726 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | JARRATT STREET | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN1 2BS | SP (DFES) | 13.1278 | 13.1058 | 13.0858 | 13.0648 | 13.0438 | 13.0178 | 12.9878 | 12.9508 | 12.9088 | 12.8608 | 12.6048 | 12.3488 | 12.1008 | 11.8668 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KEDDINGTON ROAD | 11 | 33 | Wold Newton | KEADBY | LN11 0DE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KEIGHLEY | 11 | 132 | Keighley | BRADFORD WEST | BD21 5AJ | SP (DFES) | 30.4389 | 30.4199 | 30.4019 | 30.3829 | 30.3639 | 30.3409 | 30.3129 | 30.2799 | 30.2419 | 30.1989 | 29.9749 | 29.7389 | 29.5119 | 29.2989 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KENMORE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 0XE | SP (DFES) | 18.8989 | 18.8849 | 18.8719 | 18.8579 | 18.8439 | 18.8279 | 18.8079 | 18.7839 | 18.7569 | 18.7249 | 18.5579 | 18.3919 | 18.2309 | 18.0779 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KILLINGHALL ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD3 8HN | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KILNHURST | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S64 5TL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KING GEORGE DOCK | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5PL | SP (DFES) | 23.86 | 23.859 | 23.857 | 23.855 | 23.854 | 23.851 | 23.849 | 23.846 | 23.842 | 23.839 | 23.818 | 23.797 | 23.776 | 23.756 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRK DRIVE | 11 | 33 | Menston | BRADFORD WEST | BD17 6SA | SP (DFES) | 1.0804 | 1.0574 | 1.0354 | 1.0124 | 0.98938 | 0.96038 | 0.92638 | 0.88638 | 0.83938 | 0.78738 | 0.51438 | 0.22538 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRK SANDALL | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 1QP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIRKBURN | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 9EH | SP (DFES) | 6.1762 | 6.1612 | 6.1472 | 6.1342 | 6.1212 | 6.1052 | 6.0862 | 6.0632 | 6.0362 | 6.0042 | 5.8292 | 5.6772 | 5.5242 | 5.3792 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KIVETON PARK | 11 | 66 | Thurcroft | THURCROFT | S26 6RP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | KNOSTROP | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0PJ | SP (DFES) | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEA ROAD | 11 | 33 | Blyton | KEADBY | DN21 1ND | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEASOWE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 2EY | SP (DFES) | 6.862 | 6.844 | 6.826 | 6.808 | 6.79 | 6.768 | 6.741 | 6.71 | 6.674 | 6.632 | 6.417 | 6.191 | 5.975 | 5.771 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEDSTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF10 2AX | SP (DFES) | 1.3398 | 1.3138 | 1.2868 | 1.2608 | 1.2338 | 1.2018 | 1.1618 | 1.1158 | 1.0618 | 1.0018 | 0.6828 | 0.3518 | 0.032795 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS ROAD | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 5AA | SP (DFES) | 0.40049 | 0.38949 | 0.37749 | 0.36649 | 0.35449 | 0.34049 | 0.32349 | 0.30349 | 0.28049 | 0.25449 | 0.11649 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEGRAMS MILL LANE | 11 | 33 | Girlington | BRADFORD WEST | BD7 2BA | SP (DFES) | 21.2598 | 21.2408 | 21.2218 | 21.2018 | 21.1828 | 21.1588 | 21.1298 | 21.0968 | 21.0578 | 21.0138 | 20.7848 | 20.5428 | 20.3108 | 20.0918 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LEYLANDS ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS2 7QB | SP (DFES) | 16.1552 | 16.1502 | 16.1452 | 16.1402 | 16.1342 | 16.1282 | 16.1202 | 16.1112 | 16.1002 | 16.0882 | 16.0252 | 15.9592 | 15.8952 | 15.8362 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LIVERSEDGE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF15 7NY | SP (DFES) | 1.7979 | 1.7779 | 1.7569 | 1.7369 | 1.7159 | 1.6909 | 1.6609 | 1.6249 | 1.5839 | 1.5369 | 1.2929 | 1.0369 | 0.79088 | 0.55988 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOUTH | 11 | 33 | Wold Newton | KEADBY | LN11 0WA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOW MOOR | 11 | 33 | Staygate | SKELTON GRANGE | BD12 0NG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOWFIELDS | 11 | 33 | Brighouse 132/33kV | ELLAND | HX5 9DE | SP (DFES) | 25.258 | 25.257 | 25.257 | 25.256 | 25.255 | 25.255 | 25.253 | 25.252 | 25.251 | 25.249 | 25.241 | 25.232 | 25.224 | 25.216 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | LOXLEY ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 6SJ | SP (DFES) | 0.25026 | 0.24826 | 0.24626 | 0.24426 | 0.24226 | 0.24026 | 0.23726 | 0.23426 | 0.23026 | 0.22626 | 0.20426 | 0.18126 | 0.15826 | 0.13726 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANCHESTER ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD5 0QL | SP (DFES) | 3.0907 | 3.0847 | 3.0787 | 3.0737 | 3.0677 | 3.0607 | 3.0517 | 3.0417 | 3.0297 | 3.0167 | 2.9477 | 2.8737 | 2.8037 | 2.7387 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 1 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S12 2DL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 2 | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S12 2DL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARKHAM GATES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 2FS | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARMION ROAD | 11 | 33 | Norton Lees | NORTON LEES | S11 8TS | SP (DFES) | 2.6778 | 2.6368 | 2.5958 | 2.5538 | 2.5118 | 2.4598 | 2.3968 | 2.3238 | 2.2398 | 2.1448 | 1.6468 | 1.1208 | 0.6158 | 0.1418 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARSDEN ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN31 3SQ | SP (DFES) | 5.0389 | 5.0199 | 5.0019 | 4.9839 | 4.9659 | 4.9429 | 4.9159 | 4.8839 | 4.8469 | 4.8049 | 4.5809 | 4.3559 | 4.1369 | 3.9309 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MARTONGATE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 6RX | SP (DFES) | 0 | 0 | 0 | 19.5545 | 19.4955 | 19.4245 | 19.3375 | 19.2325 | 19.1105 | 18.9695 | 18.2025 | 17.4865 | 16.7805 | 16.1185 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MELTHAM | 11 | 33 | Lindley | ELLAND | HD9 4AL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MEXBOROUGH 1_2 | 11 | 66 | Thurcroft | THURCROFT | S64 0JD | SP (DFES) | 24.708 | 24.653 | 24.599 | 24.544 | 24.49 | 24.423 | 24.343 | 24.248 | 24.138 | 24.012 | 23.344 | 22.675 | 22.025 | 21.414 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MIDDLETON TOWN STREET | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS10 3TQ | SP (DFES) | 16.422 | 16.393 | 16.364 | 16.334 | 16.304 | 16.267 | 16.223 | 16.171 | 16.111 | 16.044 | 15.687 | 15.316 | 14.958 | 14.622 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILLHOUSES | 11 | 33 | Jordanthorpe | JORDANTHORPE | S7 2QH | SP (DFES) | 1.2905 | 1.2755 | 1.2605 | 1.2455 | 1.2295 | 1.2115 | 1.1885 | 1.1615 | 1.1305 | 1.0965 | 0.91452 | 0.72252 | 0.53852 | 0.36552 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILLROYD STREET | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1JZ | SP (DFES) | 14.3477 | 14.3187 | 14.2887 | 14.2587 | 14.2297 | 14.1937 | 14.1497 | 14.0987 | 14.0387 | 13.9717 | 13.6217 | 13.2517 | 12.8967 | 12.5637 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MILTON PLACE | 11 | 33 | Wakefield North | SKELTON GRANGE | WF5 9EG | SP (DFES) | 18.7227 | 18.6857 | 18.6497 | 18.6127 | 18.5757 | 18.5307 | 18.4757 | 18.4117 | 18.3377 | 18.2517 | 17.8007 | 17.3487 | 16.9087 | 16.4937 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MIRFIELD | 11 | 33 | Thornhill 132kV | ELLAND | WF14 8NF | SP (DFES) | 19.61 | 19.574 | 19.538 | 19.501 | 19.464 | 19.419 | 19.364 | 19.301 | 19.227 | 19.143 | 18.705 | 18.246 | 17.806 | 17.391 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MONCKTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S71 4BG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOOR ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS6 4BJ | SP (DFES) | 23.2906 | 23.2526 | 23.2146 | 23.1756 | 23.1376 | 23.0896 | 23.0316 | 22.9646 | 22.8866 | 22.7976 | 22.3346 | 21.8506 | 21.3856 | 20.9486 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOORSIDE ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD2 3RJ | SP (DFES) | 20.2489 | 20.2149 | 20.1799 | 20.1449 | 20.1099 | 20.0659 | 20.0139 | 19.9519 | 19.8819 | 19.8019 | 19.3829 | 18.9409 | 18.5179 | 18.1199 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MORLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 9HS | SP (DFES) | 19.8857 | 19.8577 | 19.8287 | 19.7997 | 19.7697 | 19.7337 | 19.6907 | 19.6397 | 19.5807 | 19.5137 | 19.1637 | 18.7987 | 18.4477 | 18.1167 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MOUNT STREET | 11 | 33 | Bradford | BRADFORD WEST | BD4 8TB | SP (DFES) | 21.024 | 21.015 | 21.007 | 20.999 | 20.99 | 20.98 | 20.968 | 20.953 | 20.936 | 20.917 | 20.817 | 20.712 | 20.612 | 20.517 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | MYTHOLMROYD | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 8NE | SP (DFES) | 13.7981 | 13.7821 | 13.7661 | 13.7491 | 13.7331 | 13.7131 | 13.6881 | 13.6601 | 13.6271 | 13.5901 | 13.3961 | 13.1911 | 12.9951 | 12.8101 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NAB LANE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 9NE | SP (DFES) | 12.0246 | 12.0066 | 11.9886 | 11.9696 | 11.9516 | 11.9286 | 11.9016 | 11.8696 | 11.8326 | 11.7906 | 11.5716 | 11.3416 | 11.1216 | 10.9136 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NABWOOD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD18 4AA | SP (DFES) | 13.4641 | 13.4371 | 13.4101 | 13.3831 | 13.3561 | 13.3221 | 13.2821 | 13.2351 | 13.1801 | 13.1181 | 12.7951 | 12.4551 | 12.1281 | 11.8211 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NATIONAL AVENUE | 11 | 33 | Hull South | CREYKE BECK | HU5 4JN | SP (DFES) | 0.80537 | 0.78937 | 0.77337 | 0.75737 | 0.74137 | 0.72137 | 0.69637 | 0.66837 | 0.63537 | 0.59837 | 0.40637 | 0.20237 | 0.0063735 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | Wincobank | WINCOBANK | S61 2DL | SP (DFES) | 18.9902 | 18.9642 | 18.9392 | 18.9132 | 18.8882 | 18.8562 | 18.8192 | 18.7742 | 18.7222 | 18.6632 | 18.3492 | 18.0352 | 17.7292 | 17.4412 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEW ORCHARD LANE | 11 | 66 | Thurcroft | THURCROFT | S66 9HY | SP (DFES) | 1.2542 | 1.2312 | 1.2092 | 1.1872 | 1.1652 | 1.1382 | 1.1052 | 1.0662 | 1.0222 | 0.97015 | 0.69815 | 0.42615 | 0.16215 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWHALL ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 2RS | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5513 | 1.5353 | 1.5173 | 1.4203 | 1.3183 | 1.2213 | 1.1293 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 1 | 11 | 33 | Hull West | CREYKE BECK | HU15 2QU | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 2 | 11 | 33 | Osgodby 3/4 | DRAX | HU15 2QU | SP (DFES) | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NINELANDS LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS25 2PE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORFOLK PARK | 11 | 33 | Norton Lees | NORTON LEES | S2 3UU | SP (DFES) | 0.65239 | 0.62139 | 0.59039 | 0.55939 | 0.52839 | 0.48939 | 0.44239 | 0.38839 | 0.32539 | 0.25439 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORMANBY | 11 | 33 | Blyton | KEADBY | LN8 2HQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORMANTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF6 2JA | SP (DFES) | 4.6557 | 4.6267 | 4.5987 | 4.5707 | 4.5427 | 4.5087 | 4.4667 | 4.4177 | 4.3607 | 4.2957 | 3.9487 | 3.6047 | 3.2687 | 2.9527 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORTH AVENUE | 11 | 33 | Menston | BRADFORD WEST | LS21 1SX | SP (DFES) | 19.2526 | 19.2266 | 19.2016 | 19.1746 | 19.1486 | 19.1166 | 19.0776 | 19.0316 | 18.9786 | 18.9196 | 18.6056 | 18.2786 | 17.9636 | 17.6676 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORTH THORESBY | 11 | 33 | Wold Newton | KEADBY | DN36 5SB | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | NORWOOD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 9JR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OAKES ROAD | 11 | 33 | Lindley | ELLAND | HD3 3EW | SP (DFES) | 2.5798 | 2.5478 | 2.5158 | 2.4838 | 2.4518 | 2.4128 | 2.3648 | 2.3088 | 2.2448 | 2.1718 | 1.7898 | 1.3878 | 1.0038 | 0.64182 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OAKWOOD LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 3LF | SP (DFES) | 19.6081 | 19.5851 | 19.5621 | 19.5381 | 19.5151 | 19.4861 | 19.4511 | 19.4101 | 19.3631 | 19.3101 | 19.0301 | 18.7371 | 18.4561 | 18.1911 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ODSAL | 11 | 33 | Staygate | SKELTON GRANGE | BD6 1BW | SP (DFES) | 2.7296 | 2.7006 | 2.6716 | 2.6416 | 2.6116 | 2.5756 | 2.5316 | 2.4796 | 2.4206 | 2.3526 | 2.0006 | 1.6296 | 1.2736 | 0.9386 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OLYMPIA MILLS | 11 | 33 | Osgodby 3/4 | DRAX | YO8 7AG | SP (DFES) | 19.8721 | 19.8281 | 19.7881 | 19.7461 | 19.7081 | 19.6611 | 19.6031 | 19.5351 | 19.4541 | 19.3601 | 18.8481 | 18.3811 | 17.9171 | 17.4821 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ORGREAVE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 9NA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | OUTWOOD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF3 3TA | SP (DFES) | 1.8717 | 1.8417 | 1.8127 | 1.7827 | 1.7527 | 1.7167 | 1.6727 | 1.6207 | 1.5607 | 1.4917 | 1.1297 | 0.76366 | 0.40766 | 0.073663 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK HILL | 11 | 33 | Sheffield City | SHEFFIELD CITY | S2 5QY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6422 | 1.6162 | 1.5882 | 1.4382 | 1.2802 | 1.1282 | 0.98523 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK ROAD | 11 | 33 | Thornhill 132kV | ELLAND | WF12 9LW | SP (DFES) | 1.2208 | 1.1948 | 1.1688 | 1.1428 | 1.1168 | 1.0838 | 1.0448 | 0.99883 | 0.94583 | 0.88583 | 0.57183 | 0.24283 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PARK STREET | 11 | 132 | Park Street | WEST MELTON / THORPE MARSH | S61 1TF | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PASTURE ROAD SOUTH | 11 | 33 | Santon | KEADBY | DN18 5RX | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PATRINGTON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0AD | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 6BG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 2FL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PLANGEO | 11 | 33 | Hull South | CREYKE BECK | HU3 6EG | SP (DFES) | 3.6274 | 3.5954 | 3.5624 | 3.5294 | 3.4964 | 3.4554 | 3.4054 | 3.3474 | 3.2814 | 3.2054 | 2.8124 | 2.3954 | 1.9954 | 1.6194 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | POLLINGTON | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | DN14 0RR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0JG | SP (DFES) | 1.7538 | 1.7458 | 1.7378 | 1.7308 | 1.7228 | 1.7128 | 1.7018 | 1.6878 | 1.6728 | 1.6548 | 1.5618 | 1.4648 | 1.3718 | 1.2838 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | POOL | 11 | 33 | Menston | BRADFORD WEST | LS21 1RP | SP (DFES) | 16.4035 | 16.3975 | 16.3915 | 16.3865 | 16.3805 | 16.3735 | 16.3655 | 16.3555 | 16.3445 | 16.3315 | 16.2595 | 16.1925 | 16.1265 | 16.0635 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PRINCE OF WALES | 11 | 33 | Featherstone | FERRYBRIDGE B | WF8 4PR | SP (DFES) | 10.9345 | 10.9015 | 10.8695 | 10.8375 | 10.8055 | 10.7655 | 10.7185 | 10.6625 | 10.5975 | 10.5225 | 10.1255 | 9.7315 | 9.3475 | 8.9865 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | PROSPECT ROAD | 11 | 33 | Lindley | ELLAND | HD3 4UY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | QUEENS ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 2LZ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | QUEENSBURY | 11 | 33 | Holmfield | BRADFORD WEST | HX3 7TJ | SP (DFES) | 25.5904 | 25.5504 | 25.5114 | 25.4714 | 25.4314 | 25.3824 | 25.3234 | 25.2544 | 25.1744 | 25.0844 | 24.6124 | 24.1124 | 23.6344 | 23.1854 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWCLIFFE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8PQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWDON | 11 | 33 | Rodley | SKELTON GRANGE | LS19 7BZ | SP (DFES) | 23.9166 | 23.8906 | 23.8646 | 23.8386 | 23.8116 | 23.7796 | 23.7406 | 23.6946 | 23.6416 | 23.5816 | 23.2666 | 22.9366 | 22.6206 | 22.3236 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | Rawmarsh Road 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | Rawmarsh Road 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON ROAD | 11 | 33 | Girlington | BRADFORD WEST | BD1 3SH | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON SPRING ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 1PD | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5828 | 3.5548 | 3.5238 | 3.3588 | 3.1838 | 3.0168 | 2.8598 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | REVILL LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 7QX | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROCKWARE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4RH | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY LANE | 11 | 33 | Rodley | SKELTON GRANGE | LS13 1LJ | SP (DFES) | 0.81121 | 0.78221 | 0.75321 | 0.72321 | 0.69321 | 0.65721 | 0.61221 | 0.56121 | 0.50121 | 0.43321 | 0.078205 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROMAN AVENUE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 2DY | SP (DFES) | 20.5436 | 20.5196 | 20.4946 | 20.4706 | 20.4456 | 20.4146 | 20.3776 | 20.3346 | 20.2846 | 20.2286 | 19.9326 | 19.6226 | 19.3256 | 19.0456 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | ROYDS LANE | 11 | 33 | Wakefield North | SKELTON GRANGE | LS26 0BE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | SP (DFES) | 11.9278 | 11.9178 | 11.9088 | 11.8988 | 11.8888 | 11.8768 | 11.8618 | 11.8448 | 11.8258 | 11.8028 | 11.6868 | 11.5638 | 11.4468 | 11.3368 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAINT STREET | 11 | 33 | Girlington | BRADFORD WEST | BD7 4EH | SP (DFES) | 12.4566 | 12.4396 | 12.4226 | 12.4056 | 12.3876 | 12.3666 | 12.3406 | 12.3096 | 12.2746 | 12.2356 | 12.0286 | 11.8096 | 11.5996 | 11.4026 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTERFORTH | 11 | 33 | Silsden | BRADFORD WEST | BB18 6JD | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTERHEBBLE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX3 0QH | SP (DFES) | 19.6036 | 19.5746 | 19.5436 | 19.5136 | 19.4836 | 19.4466 | 19.4016 | 19.3496 | 19.2886 | 19.2206 | 18.8636 | 18.4846 | 18.1226 | 17.7826 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SALTSHOUSE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU8 9HR | SP (DFES) | 21.3912 | 21.3702 | 21.3492 | 21.3272 | 21.3062 | 21.2792 | 21.2472 | 21.2092 | 21.1662 | 21.1172 | 20.8632 | 20.5922 | 20.3332 | 20.0892 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SANDHILL LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO41 4DF | SP (DFES) | 0.3317 | 0.3227 | 0.3127 | 0.3037 | 0.2947 | 0.2837 | 0.2707 | 0.2547 | 0.2367 | 0.2157 | 0.1007 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SAXON ROAD | 11 | 33 | Norton Lees | NORTON LEES | S8 0XQ | SP (DFES) | 2.3052 | 2.2752 | 2.2462 | 2.2162 | 2.1862 | 2.1492 | 2.1042 | 2.0522 | 1.9922 | 1.9232 | 1.5682 | 1.1912 | 0.83018 | 0.49118 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCARTHO | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN33 3JL | SP (DFES) | 0.24535 | 0.18135 | 0.11935 | 0.057354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCHOLES | 11 | 33 | Thornhill 132kV | ELLAND | HD9 1UG | SP (DFES) | 0.93713 | 0.91513 | 0.89413 | 0.87213 | 0.85113 | 0.82413 | 0.79213 | 0.75513 | 0.71113 | 0.66213 | 0.40513 | 0.13513 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCISSETT | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SCULCOATES A | 11 | 132 | Sculcoates A | CREYKE BECK | HU5 1DA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SEACROFT | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 1LU | SP (DFES) | 13.23 | 13.211 | 13.191 | 13.171 | 13.151 | 13.127 | 13.097 | 13.063 | 13.023 | 12.977 | 12.74 | 12.491 | 12.253 | 12.028 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SEATON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU11 5RQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SELBY | 11 | 33 | Osgodby 3/4 | DRAX | YO8 8NB | SP (DFES) | 0.77957 | 0.70757 | 0.63957 | 0.57057 | 0.50657 | 0.42757 | 0.33257 | 0.21757 | 0.082572 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SELBY ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS15 0QE | SP (DFES) | 20.0276 | 19.9946 | 19.9626 | 19.9296 | 19.8966 | 19.8556 | 19.8066 | 19.7496 | 19.6826 | 19.6076 | 19.2136 | 18.8016 | 18.4066 | 18.0336 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHARLSTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF4 1BE | SP (DFES) | 12.0817 | 12.0467 | 12.0107 | 11.9757 | 11.9397 | 11.8967 | 11.8437 | 11.7817 | 11.7097 | 11.6277 | 11.1897 | 10.7547 | 10.3307 | 9.9307 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHEPCOTE TINSLEY | 11 | 33 | Wincobank | WINCOBANK | S9 1RF | SP (DFES) | 30.0977 | 30.0977 | 30.0977 | 30.0977 | 30.0977 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHERBURN | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6PL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHIPLEY | 11 | 33 | Bradford | BRADFORD WEST | DN21 5UT | SP (DFES) | 25.9505 | 25.9295 | 25.9085 | 25.8865 | 25.8655 | 25.8385 | 25.8065 | 25.7695 | 25.7265 | 25.6775 | 25.4215 | 25.1525 | 24.8945 | 24.6515 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SHIRLAND LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3GD | SP (DFES) | 0.009 | 0.006 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILVER STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 2DU | SP (DFES) | 2.7673 | 2.7633 | 2.7583 | 2.7533 | 2.7483 | 2.7433 | 2.7353 | 2.7273 | 2.7183 | 2.7073 | 2.6513 | 2.5913 | 2.5343 | 2.4813 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SILVERWOOD | 11 | 66 | Thurcroft | THURCROFT | S65 4PR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SKILLINGS LANE | 11 | 33 | Hull West | CREYKE BECK | HU15 1EQ | SP (DFES) | 2.4154 | 2.3904 | 2.3674 | 2.3434 | 2.3214 | 2.2944 | 2.2614 | 2.2224 | 2.1754 | 2.1224 | 1.8314 | 1.5614 | 1.2934 | 1.0424 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SKIPTON | 11 | 33 | Silsden | BRADFORD WEST | BD23 2RR | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SLAITHWAITE | 11 | 33 | Lindley | ELLAND | HD7 6LS | SP (DFES) | 0.81686 | 0.79486 | 0.77386 | 0.75186 | 0.72986 | 0.70286 | 0.67086 | 0.63286 | 0.58886 | 0.53986 | 0.27986 | 0.0068618 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SLEDMERE GARTH | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 5DS | SP (DFES) | 18.759 | 18.746 | 18.733 | 18.719 | 18.706 | 18.69 | 18.67 | 18.647 | 18.62 | 18.59 | 18.432 | 18.267 | 18.108 | 17.959 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SMITH STREET | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 2RY | SP (DFES) | 12.7539 | 12.7349 | 12.7159 | 12.6959 | 12.6769 | 12.6529 | 12.6249 | 12.5909 | 12.5519 | 12.5069 | 12.2699 | 12.0319 | 11.8009 | 11.5829 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SMITHY GREEN | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SNAITHING PARK ROAD | 11 | 33 | Norton Lees | NORTON LEES | S10 3LJ | SP (DFES) | 0.16432 | 0.13832 | 0.11232 | 0.085323 | 0.059323 | 0.026323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SNELSINS LANE | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 3UH | SP (DFES) | 16.3806 | 16.3606 | 16.3406 | 16.3206 | 16.3006 | 16.2756 | 16.2456 | 16.2106 | 16.1706 | 16.1246 | 15.8846 | 15.6326 | 15.3906 | 15.1636 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH ELMSALL | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 2JH | SP (DFES) | 23.1894 | 23.1644 | 23.1404 | 23.1164 | 23.0914 | 23.0614 | 23.0254 | 22.9834 | 22.9344 | 22.8774 | 22.5774 | 22.2794 | 21.9894 | 21.7154 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH FERRIBY | 11 | 33 | Santon | KEADBY | DN18 6JL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH KIRKBY | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 3TJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH RESTON | 11 | 33 | Wold Newton | KEADBY | LN11 8JQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH STREET | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 1AH | SP (DFES) | 7.6959 | 7.6719 | 7.6479 | 7.6229 | 7.5989 | 7.5679 | 7.5309 | 7.4889 | 7.4389 | 7.3829 | 7.0909 | 6.7809 | 6.4849 | 6.2069 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHGATE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 3BE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 19.4986 | 19.4666 | 19.4296 | 19.3846 | 19.3336 | 19.0566 | 18.7986 | 18.5436 | 18.3046 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHWOOD ROAD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU16 5AN | SP (DFES) | 0.17751 | 0.12351 | 0.072507 | 0.020507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EN | SP (DFES) | 24.2262 | 24.1912 | 24.1572 | 24.1222 | 24.0882 | 24.0462 | 23.9952 | 23.9352 | 23.8662 | 23.7882 | 23.3802 | 22.9472 | 22.5342 | 22.1462 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPARK MILL LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 0TT | SP (DFES) | 5.9692 | 5.9112 | 5.8562 | 5.8002 | 5.7482 | 5.6842 | 5.6062 | 5.5132 | 5.4042 | 5.2782 | 4.5932 | 3.9542 | 3.3242 | 2.7322 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPENBOROUGH | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 5BT | SP (DFES) | 16.5855 | 16.5565 | 16.5265 | 16.4965 | 16.4665 | 16.4295 | 16.3845 | 16.3325 | 16.2715 | 16.2035 | 15.8455 | 15.4695 | 15.1085 | 14.7695 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SPRING MILL STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD5 7HF | SP (DFES) | 3.5058 | 3.4928 | 3.4798 | 3.4668 | 3.4538 | 3.4368 | 3.4178 | 3.3948 | 3.3678 | 3.3378 | 3.1818 | 3.0168 | 2.8578 | 2.7088 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAINFORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN7 5HG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STAIRFOOT | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 5AD | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STANLEY STREET | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S3 8HG | SP (DFES) | 3.1223 | 3.1143 | 3.1053 | 3.0953 | 3.0863 | 3.0753 | 3.0613 | 3.0463 | 3.0273 | 3.0063 | 2.8983 | 2.7843 | 2.6743 | 2.5713 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STANNINGTON ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 5FH | SP (DFES) | 1.8226 | 1.7786 | 1.7346 | 1.6906 | 1.6456 | 1.5896 | 1.5236 | 1.4456 | 1.3556 | 1.2546 | 0.72362 | 0.16162 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STATION ROAD | 11 | 33 | Scunthorpe North | KEADBY | DN15 6BT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STEVENSON ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 3XG | SP (DFES) | 1.1752 | 1.1752 | 1.1752 | 1.1752 | 1.1752 | 1.1752 | 1.1752 | 1.1752 | 1.1742 | 1.1742 | 1.1742 | 1.1732 | 1.1732 | 1.1722 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOKE STREET | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3QN | SP (DFES) | 0.146 | 0.146 | 0.146 | 0.145 | 0.145 | 0.145 | 0.144 | 0.144 | 0.144 | 0.143 | 0.14 | 0.138 | 0.135 | 0.132 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 132/11KV | 11 | 132 | Stourton 132/11kV | SKELTON GRANGE | LS10 1SP | SP (DFES) | 1.2741 | 1.2741 | 1.2731 | 1.2721 | 1.2711 | 1.2701 | 1.2691 | 1.2681 | 1.2661 | 1.2641 | 1.2551 | 1.2451 | 1.2361 | 1.2271 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 33/11KV | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1AX | SP (DFES) | 5.617 | 5.605 | 5.593 | 5.581 | 5.568 | 5.553 | 5.535 | 5.514 | 5.489 | 5.461 | 5.314 | 5.161 | 5.013 | 4.874 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | STOW | 11 | 33 | Blyton | KEADBY | LN1 2AJ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWAN BANK LANE | 11 | 33 | Halifax 132/33kV | ELLAND | HX3 9XT | SP (DFES) | 1.4153 | 1.3953 | 1.3753 | 1.3543 | 1.3343 | 1.3093 | 1.2793 | 1.2433 | 1.2023 | 1.1563 | 0.91335 | 0.65835 | 0.41435 | 0.18535 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWEET STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9TZ | SP (DFES) | 7.653 | 7.649 | 7.646 | 7.643 | 7.639 | 7.635 | 7.63 | 7.624 | 7.617 | 7.609 | 7.568 | 7.525 | 7.484 | 7.445 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | SWINNOW MOOR | 11 | 33 | Rodley | SKELTON GRANGE | LS13 4RJ | SP (DFES) | 2.3895 | 2.3605 | 2.3305 | 2.3005 | 2.2705 | 2.2335 | 2.1885 | 2.1365 | 2.0765 | 2.0075 | 1.6495 | 1.2745 | 0.91447 | 0.57547 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TADCASTER | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9PA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TANKERSLEY PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 2PT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S60 1AD | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNBURY | 11 | 33 | Rodley | SKELTON GRANGE | BD3 7AD | SP (DFES) | 5.0333 | 5.0093 | 4.9853 | 4.9613 | 4.9373 | 4.9083 | 4.8723 | 4.8303 | 4.7823 | 4.7273 | 4.4423 | 4.1403 | 3.8513 | 3.5803 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN8 4NA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORNTON | 11 | 33 | Holmfield | BRADFORD WEST | BD13 3DP | SP (DFES) | 20.0022 | 19.9622 | 19.9222 | 19.8812 | 19.8402 | 19.7902 | 19.7292 | 19.6592 | 19.5772 | 19.4852 | 19.0022 | 18.4912 | 18.0032 | 17.5432 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | THORPE ROAD | 11 | 33 | Osgodby 3/4 | DRAX | DN14 7PA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TICKHILL ROAD | 11 | 66 | Thurcroft | THURCROFT | S66 7QN | SP (DFES) | 29.1104 | 29.0744 | 29.0394 | 29.0044 | 28.9694 | 28.9264 | 28.8744 | 28.8134 | 28.7414 | 28.6604 | 28.2274 | 27.7974 | 27.3784 | 26.9844 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINGLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | WF3 1SS | SP (DFES) | 0.12561 | 0.098615 | 0.070615 | 0.042615 | 0.014615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY PARK ROAD | 11 | 33 | Wincobank | WINCOBANK | S9 5DL | SP (DFES) | 2.8597 | 2.8587 | 2.8567 | 2.8547 | 2.8527 | 2.8507 | 2.8477 | 2.8447 | 2.8407 | 2.8367 | 2.8147 | 2.7917 | 2.7697 | 2.7487 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1TY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TIVERTON ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 4DA | SP (DFES) | 1.4731 | 1.4501 | 1.4261 | 1.4031 | 1.3791 | 1.3501 | 1.3141 | 1.2731 | 1.2251 | 1.1711 | 0.89014 | 0.59214 | 0.30614 | 0.037138 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TODMORDEN | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | OL14 7NB | SP (DFES) | 12.83 | 12.807 | 12.784 | 12.761 | 12.738 | 12.71 | 12.676 | 12.636 | 12.59 | 12.538 | 12.265 | 11.977 | 11.701 | 11.442 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TOLLER LANE | 11 | 33 | Girlington | BRADFORD WEST | BD9 5LE | SP (DFES) | 21.3042 | 21.2792 | 21.2552 | 21.2302 | 21.2052 | 21.1742 | 21.1372 | 21.0942 | 21.0442 | 20.9872 | 20.6912 | 20.3782 | 20.0792 | 19.7972 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | TONG STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9PP | SP (DFES) | 3.2742 | 3.2622 | 3.2482 | 3.2352 | 3.2222 | 3.2062 | 3.1862 | 3.1632 | 3.1362 | 3.1062 | 2.9492 | 2.7832 | 2.6232 | 2.4742 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | UPPER BASINGHALL STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS1 5JS | SP (DFES) | 4.338 | 4.336 | 4.334 | 4.332 | 4.33 | 4.328 | 4.325 | 4.321 | 4.317 | 4.312 | 4.287 | 4.262 | 4.237 | 4.214 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | VARLEY STREET | 11 | 33 | Rodley | SKELTON GRANGE | LS28 6AN | SP (DFES) | 22.7204 | 22.6944 | 22.6674 | 22.6414 | 22.6144 | 22.5814 | 22.5424 | 22.4954 | 22.4424 | 22.3814 | 22.0624 | 21.7304 | 21.4104 | 21.1094 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | VICTORIA STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4DP | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61542 | 0.60242 | 0.58842 | 0.51642 | 0.44042 | 0.36642 | 0.29742 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WALESBY | 11 | 33 | Wold Newton | KEADBY | LN8 3UL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WARREN LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9NT | SP (DFES) | 3.8858 | 3.8788 | 3.8718 | 3.8648 | 3.8578 | 3.8488 | 3.8388 | 3.8268 | 3.8128 | 3.7968 | 3.7128 | 3.6268 | 3.5438 | 3.4648 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WATH UPON DEARNE | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DX | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | Wincobank | WINCOBANK | S60 5BL | SP (DFES) | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5026 | 30.5026 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WAWNE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 5BT | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEELAND ROAD | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 0LA | SP (DFES) | 7.1861 | 7.1731 | 7.1611 | 31.2966 | 31.2846 | 31.2696 | 31.2516 | 31.2306 | 31.2066 | 31.1786 | 31.0296 | 30.8816 | 30.7376 | 30.6016 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WELLINGTON STREET | 11 | 33 | Featherstone | FERRYBRIDGE B | WF10 1NW | SP (DFES) | 12.9581 | 12.9371 | 12.9171 | 12.8971 | 12.8761 | 12.8511 | 12.8211 | 12.7861 | 12.7451 | 12.6971 | 12.4471 | 12.1981 | 11.9551 | 11.7261 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WESLEY CRESCENT | 11 | 33 | Humberston | GRIMSBY WEST | DN35 0JU | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST DOCKS | 11 | 33 | Hull South | CREYKE BECK | HU3 4UU | SP (DFES) | 1.7763 | 1.7753 | 1.7743 | 1.7733 | 1.7723 | 1.7713 | 1.7693 | 1.7673 | 1.7653 | 1.7633 | 1.7503 | 1.7363 | 1.7233 | 1.7113 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST END LANE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN11 0PU | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST MOOR PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3FE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WEST PARK | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 5PS | SP (DFES) | 7.1026 | 7.0816 | 7.0606 | 7.0396 | 7.0186 | 6.9926 | 6.9606 | 6.9236 | 6.8816 | 6.8326 | 6.5796 | 6.3146 | 6.0596 | 5.8206 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WESTCOTT STREET | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU8 8JN | SP (DFES) | 1.0089 | 0.97089 | 0.93289 | 0.89389 | 0.85489 | 0.80589 | 0.74789 | 0.67889 | 0.60089 | 0.51189 | 0.047887 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHEATACRE ROAD | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 2GQ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHEATLEY PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4PG | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHINGATE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 3QT | SP (DFES) | 19.9011 | 19.8841 | 19.8671 | 19.8491 | 19.8321 | 19.8101 | 19.7841 | 19.7541 | 19.7181 | 19.6781 | 19.4691 | 19.2501 | 19.0401 | 18.8421 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITE LEE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 8AF | SP (DFES) | 1.9715 | 1.9355 | 1.8985 | 1.8615 | 1.8245 | 1.7785 | 1.7235 | 1.6595 | 1.5845 | 1.5005 | 1.0585 | 0.5945 | 0.1495 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | Low Road | SKELTON GRANGE | LS1 4HR | SP (DFES) | 7.776 | 7.776 | 7.775 | 7.774 | 7.773 | 7.772 | 7.77 | 7.769 | 7.767 | 7.765 | 7.753 | 7.742 | 7.731 | 7.72 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS1 4BN | SP (DFES) | 18.7049 | 18.7029 | 18.7019 | 18.6999 | 18.6989 | 18.6969 | 18.6949 | 18.6919 | 18.6889 | 18.6859 | 18.6679 | 18.6489 | 18.6309 | 18.6139 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WIBSEY | 11 | 33 | Staygate | SKELTON GRANGE | BD6 3BG | SP (DFES) | 0.64726 | 0.61226 | 0.57726 | 0.54226 | 0.50626 | 0.46226 | 0.41026 | 0.34826 | 0.27626 | 0.19626 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WITHERNSEA | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU19 2QA | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOODCOCK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 5LL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOODSEATS | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 8QB | SP (DFES) | 2.2407 | 2.2127 | 2.1847 | 2.1567 | 2.1277 | 2.0927 | 2.0507 | 2.0007 | 1.9437 | 1.8787 | 1.5407 | 1.1827 | 0.84069 | 0.51769 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WOOLLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 5JE | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WORSBROUGH PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S70 5LY | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | WRAWBY | 11 | 33 | Santon | KEADBY | DN20 8SX | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4BL | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YEW GREEN ROAD | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD4 5DD | SP (DFES) | 1.393 | 1.367 | 1.34 | 1.313 | 1.287 | 1.254 | 1.214 | 1.168 | 1.114 | 1.053 | 0.73397 | 0.39997 | 0.079969 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YORK ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 6TF | SP (DFES) | 20.8211 | 20.7901 | 20.7591 | 20.7271 | 20.6951 | 20.6551 | 20.6081 | 20.5521 | 20.4881 | 20.4151 | 20.0341 | 19.6351 | 19.2521 | 18.8911 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgY | YORK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 3AZ | SP (DFES) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NG FES - Steady Progression (EE CF assumptions) | Network Capacity Generation Headroom (MVA)
NPgN | ANNFIELD | 66 | 132 | Annfield | STELLA SOUTH | DH9 7XW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BARRACK ROAD | 33 | 132 | Barrack Road | STELLA NORTH | NE4 6DB | NZE (DFES Best View Scenario) | 114.328 | 114.015 | 113.665 | 113.288 | 112.867 | 112.417 | 111.982 | 111.562 | 111.148 | 110.742 | 109.114 | 107.95 | 107.29 | 106.73 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER | 33 | 132 | Blucher | STELLA NORTH | NE15 9SD | NZE (DFES Best View Scenario) | 94.003 | 93.305 | 92.474 | 91.769 | 91.021 | 90.199 | 89.397 | 88.64 | 87.957 | 87.234 | 84.737 | 82.557 | 81.387 | 80.415 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD | 33 | 132 | Bowesfield | NORTON | TS18 3HP | NZE (DFES Best View Scenario) | 61.151 | 58.685 | 55.422 | 53.833 | 52.488 | 50.808 | 49.111 | 47.689 | 46.929 | 45.652 | 44.815 | 40.341 | 38.689 | 37.587 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CHIRTON GRANGE | 33 | 132 | Chirton Grange | TYNEMOUTH | NE29 8EY | NZE (DFES Best View Scenario) | 61.52 | 60.873 | 60.131 | 59.403 | 58.605 | 57.745 | 56.909 | 56.108 | 55.342 | 54.571 | 51.623 | 49.359 | 48.092 | 47.022 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | COALBURNS | 66 | 132 | Coalburns | STELLA SOUTH | NE40 4JP | NZE (DFES Best View Scenario) | 69.646 | 67.433 | 64.37 | 63.317 | 62.642 | 61.634 | 60.57 | 59.79 | 59.761 | 59.104 | 61.412 | 58.479 | 57.757 | 57.452 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL | 33 | 132 | Darlington Central | NORTON | DL1 1HG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON NORTH | 33 | 132 | Darlington North | NORTON | DL3 0XE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON | 66 | 132 | Dunston | STELLA NORTH | NE11 9DH | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH | 33 | 132 | Flatworth | TYNEMOUTH | NE29 7FN | NZE (DFES Best View Scenario) | 27.06 | 26.751 | 26.402 | 26.039 | 25.635 | 25.203 | 24.785 | 24.382 | 23.99 | 23.602 | 22.073 | 20.956 | 20.329 | 19.799 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH | 33 | 132 | Gosforth | TYNEMOUTH | NE3 1XL | NZE (DFES Best View Scenario) | 88.47 | 87.9 | 87.254 | 86.592 | 85.859 | 85.073 | 84.311 | 83.579 | 82.869 | 82.165 | 79.412 | 77.378 | 76.24 | 75.282 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/33KV | 33 | 132 | Harrogate 132/33kV | KNARESBOROUGH | HG1 2LA | NZE (DFES Best View Scenario) | 45.483 | 44.731 | 43.811 | 43.119 | 42.41 | 41.613 | 40.827 | 40.094 | 39.462 | 38.753 | 36.503 | 34.223 | 32.965 | 31.898 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE | 33 | 132 | Husthwaite | KNARESBOROUGH | YO61 4PN | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | Leeming Bar_Skeeby | NORTON | DL7 0RL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | LINTON | 66 | 132 | Linton | BLYTH 132kV | NE61 5DA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MALTON GRID | 66 | 132 | Malton Grid | OSBALDWICK | YO17 6RD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 132/33kV | 33 | 132 | Melrosegate | OSBALDWICK | YO31 0YB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES | 66 | 132 | North Tees | NORTON | TS23 1PY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE 132/66kV | 66 | 132 | Potter House | SPENNYMOOR | DH1 5FF | NZE (DFES Best View Scenario) | 88.684 | 87.262 | 85.46 | 84.326 | 83.238 | 81.972 | 80.715 | 79.585 | 78.734 | 77.673 | 75.157 | 71.684 | 70.011 | 68.684 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSWORTH | 66 | 132 | Ravensworth | STELLA SOUTH | DH3 1RQ | NZE (DFES Best View Scenario) | 76.138 | 75.655 | 75.043 | 74.659 | 74.29 | 73.862 | 73.437 | 73.057 | 72.774 | 72.42 | 71.607 | 70.47 | 69.947 | 69.543 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH GRID | 33 | 132 | Scarborough Grid | OSBALDWICK | YO11 2YH | NZE (DFES Best View Scenario) | 70.668 | 68.655 | 66.008 | 64.668 | 63.507 | 62.072 | 60.623 | 59.384 | 58.657 | 57.518 | 56.232 | 52.19 | 50.474 | 49.2 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SEAL SANDS | 66 | 132 | Seal Sands | SALTHOLME | TS2 1FB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5LJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO | 66 | 132 | Toronto | SPENNYMOOR | DL14 7RJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 3PS | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ATTERCLIFFE | 33 | 132 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3FA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 132/66KV | 66 | 132 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6NJ | NZE (DFES Best View Scenario) | 66.9144 | 65.8474 | 64.3714 | 63.5444 | 62.8564 | 61.9134 | 60.9234 | 60.0404 | 59.4274 | 58.5974 | 56.2344 | 53.6514 | 52.2334 | 51.0174 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BEVERLEY 132/33KV | 33 | 132 | Beverley 132/33kV | CREYKE BECK | HU17 0RW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 132/33KV | 33 | 132 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | NZE (DFES Best View Scenario) | 9.5386 | 9.0286 | 8.4456 | 7.8526 | 7.2006 | 6.4946 | 5.8066 | 5.1396 | 4.4896 | 3.8376 | 1.2246 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS B | 33 | 132 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1DA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BLYTON | 33 | 132 | Blyton | KEADBY | DN21 3NS | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BRADFORD | 33 | 132 | Bradford | BRADFORD WEST | BD1 4RF | NZE (DFES Best View Scenario) | 99.226 | 98.599 | 97.897 | 97.141 | 96.299 | 95.398 | 94.524 | 93.673 | 92.829 | 91.995 | 88.598 | 86.116 | 84.631 | 83.337 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHAM | 33 | 132 | Bramham | FERRYBRIDGE B | LS24 9NT | NZE (DFES Best View Scenario) | 25.4807 | 22.0417 | 16.5717 | 15.0597 | 14.7267 | 13.1697 | 11.2247 | 9.7737 | 9.8197 | 8.5627 | 9.1257 | 4.4647 | 2.1867 | 0.21972 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BRANSHOLME | 33 | 132 | Bransholme | CREYKE BECK | HU7 4ZN | NZE (DFES Best View Scenario) | 65.2383 | 64.3313 | 63.0553 | 62.3853 | 61.8543 | 61.0953 | 60.2893 | 59.5773 | 59.1123 | 58.4463 | 56.6583 | 54.5543 | 53.4003 | 52.4083 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | Brighouse 132/33kV | ELLAND | HD6 1PZ | NZE (DFES Best View Scenario) | 95.4417 | 94.3297 | 92.7337 | 91.9647 | 91.4007 | 90.5387 | 89.6057 | 88.7937 | 88.3097 | 87.5487 | 85.6727 | 83.1957 | 81.8147 | 80.6107 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 8UX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DONCASTER CENTRAL | 33 | 132 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1RE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | Driffield/Beverley Group | CREYKE BECK | YO25 5NW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FEATHERSTONE | 33 | 132 | Featherstone | FERRYBRIDGE B | WF7 6HE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GIRLINGTON | 33 | 132 | Girlington | BRADFORD WEST | BD7 2NB | NZE (DFES Best View Scenario) | 84.9795 | 84.6005 | 84.1755 | 83.7185 | 83.2095 | 82.6645 | 82.1355 | 81.6205 | 81.1105 | 80.6065 | 78.5515 | 77.0505 | 76.1525 | 75.3695 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 132/33KV | 33 | 132 | Halifax 132/33kV | ELLAND | HX1 1XB | NZE (DFES Best View Scenario) | 1.3236 | 1.1186 | 0.88962 | 0.64362 | 0.37062 | 0.077619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HECKMONDWIKE | 33 | 132 | Heckmondwike | SKELTON GRANGE | WF16 9LU | NZE (DFES Best View Scenario) | 88.487 | 88.046 | 87.552 | 87.021 | 86.429 | 85.796 | 85.181 | 84.581 | 83.984 | 83.394 | 80.978 | 79.203 | 78.125 | 77.18 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HOLMFIELD | 33 | 132 | Holmfield | BRADFORD WEST | HX2 9AY | NZE (DFES Best View Scenario) | 56.7715 | 56.0885 | 55.3255 | 54.5055 | 53.5925 | 52.6165 | 51.6635 | 50.7295 | 49.7955 | 48.8665 | 45.0235 | 42.1575 | 40.3575 | 38.7545 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 132/33KV | 33 | 132 | Hull East 132/33kV | SALTEND NORTH | HU9 5NL | NZE (DFES Best View Scenario) | 8.1447 | 7.4707 | 6.7147 | 5.9127 | 5.0307 | 4.0787 | 3.1417 | 2.2137 | 1.2757 | 0.32873 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HULL SOUTH | 33 | 132 | Hull South | CREYKE BECK | HU3 5JA | NZE (DFES Best View Scenario) | 88.0022 | 87.3902 | 86.7072 | 85.9712 | 85.1522 | 84.2762 | 83.4232 | 82.5922 | 81.7652 | 80.9472 | 77.5942 | 75.1282 | 73.6272 | 72.3082 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HULL WEST | 33 | 132 | Hull West | CREYKE BECK | HU13 0FA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HUMBERSTON | 33 | 132 | Humberston | GRIMSBY WEST | DN36 4AW | NZE (DFES Best View Scenario) | 67.2121 | 66.6351 | 65.9051 | 65.3451 | 64.7921 | 64.1381 | 63.4801 | 62.8641 | 62.3291 | 61.7331 | 59.6021 | 57.7841 | 56.7231 | 55.8001 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HUNNINGLEY | 33 | 132 | Hunningley | WEST MELTON SECTION 3 | S70 3ET | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HUNSHELF | 66 | 132 | Hunshelf | WEST MELTON SECTION 3 | S36 8WR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | IMMINGHAM | 33 | 132 | Immingham | GRIMSBY WEST | DN40 1QT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KIRKHAW LANE | 33 | 132 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8SB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C 2/5 | 33 | 132 | Kirkstall C 2/5 | KIRKSTALL B | LS18 4EL | NZE (DFES Best View Scenario) | 81.8482 | 81.7192 | 81.5742 | 81.4182 | 81.2442 | 81.0582 | 80.8782 | 80.7022 | 80.5282 | 80.3562 | 79.6572 | 79.1462 | 78.8422 | 78.5772 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS18 4EL | NZE (DFES Best View Scenario) | 105.8955 | 104.8995 | 103.6915 | 102.6425 | 101.5495 | 100.3135 | 99.0895 | 97.9245 | 96.8555 | 95.7275 | 91.4655 | 88.0745 | 86.0915 | 84.3715 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS EAST | 33 | 132 | Leeds East | SKELTON GRANGE | LS9 6ED | NZE (DFES Best View Scenario) | 65.4672 | 64.5592 | 63.3442 | 62.5712 | 61.8722 | 60.9802 | 60.0622 | 59.2252 | 58.5782 | 57.7832 | 55.2572 | 52.8122 | 51.4402 | 50.2592 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS NORTH | 33 | 132 | Leeds North | SKELTON GRANGE | LS7 2AU | NZE (DFES Best View Scenario) | 107.591 | 107.181 | 106.723 | 106.229 | 105.678 | 105.09 | 104.519 | 103.963 | 103.412 | 102.868 | 100.654 | 99.039 | 98.075 | 97.237 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LINDLEY | 33 | 132 | Lindley | ELLAND | HD3 3NY | NZE (DFES Best View Scenario) | 92.0602 | 91.1822 | 90.0612 | 89.2312 | 88.4222 | 87.4542 | 86.4772 | 85.5632 | 84.7842 | 83.9032 | 80.7952 | 78.0842 | 76.4992 | 75.1172 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LOW ROAD | 33 | 132 | Low Road | SKELTON GRANGE | LS10 1RH | NZE (DFES Best View Scenario) | 1.462 | 1.092 | 0.66002 | 0.24602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MALLARD WAY | 33 | 132 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MENSTON | 33 | 132 | Menston | BRADFORD WEST | LS29 6BP | NZE (DFES Best View Scenario) | 86.6197 | 85.5717 | 84.0147 | 83.3767 | 82.9857 | 82.2827 | 81.5007 | 80.8477 | 80.5567 | 79.9637 | 78.9317 | 77.0067 | 76.0237 | 75.1917 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MOSS ROAD | 33 | 132 | Moss Road | GRIMSBY WEST | DN32 0LW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 1/2 | 33 | 132 | Osgodby 1/2 | DRAX | YO8 5HY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | OSGODBY 3/4 | 33 | 132 | Osgodby 3/4 | DRAX | YO8 5HY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY | 33 | 132 | Rodley | SKELTON GRANGE | LS13 1PZ | NZE (DFES Best View Scenario) | 121.1771 | 120.1701 | 118.7851 | 117.9881 | 117.3121 | 116.4011 | 115.4491 | 114.5951 | 113.9871 | 113.1831 | 110.8311 | 108.3331 | 106.9551 | 105.7711 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | NZE (DFES Best View Scenario) | 80.8518 | 80.3088 | 79.6918 | 79.0548 | 78.3548 | 77.5988 | 76.8598 | 76.1428 | 75.4398 | 74.7358 | 71.8898 | 69.7658 | 68.4798 | 67.3518 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SALTEND 132/33KV | 33 | 132 | Saltend 132/33kV | SALTEND NORTH | HU12 8EY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SANTON | 33 | 132 | Santon | KEADBY | DN16 1XP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE NORTH | 33 | 132 | Scunthorpe North | KEADBY | DN15 8GN | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SCUNTHORPE SOUTH | 33 | 132 | Scunthorpe South | KEADBY | DN16 1BD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SILSDEN | 33 | 132 | Silsden | BRADFORD WEST | BD20 0ND | NZE (DFES Best View Scenario) | 0 | 51.0647 | 48.3837 | 46.8907 | 45.7047 | 44.0227 | 42.1767 | 40.4087 | 38.9937 | 37.0617 | 30.0037 | 22.2117 | 16.2347 | 10.4177 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EL | NZE (DFES Best View Scenario) | 59.2604 | 58.5914 | 57.7704 | 57.0854 | 56.3854 | 55.5804 | 54.7744 | 54.0014 | 53.2924 | 52.5254 | 49.5834 | 47.1324 | 45.5834 | 44.1904 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | STAYGATE | 33 | 132 | Staygate | SKELTON GRANGE | BD6 1YA | NZE (DFES Best View Scenario) | 115.6537 | 115.1537 | 114.5937 | 113.9917 | 113.3207 | 112.6027 | 111.9057 | 111.2277 | 110.5547 | 109.8907 | 107.1837 | 105.2057 | 104.0217 | 102.9897 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | THORNHILL 132KV | 33 | 132 | Thornhill 132kV | ELLAND | WF13 3JQ | NZE (DFES Best View Scenario) | 19.0417 | 17.6447 | 15.7467 | 14.6077 | 13.6177 | 12.3117 | 10.9547 | 9.7267 | 8.8167 | 7.6507 | 4.0827 | 0.43974 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7AL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WAKEFIELD NORTH | 33 | 132 | Wakefield North | SKELTON GRANGE | WF1 3HN | NZE (DFES Best View Scenario) | 79.7204 | 78.2184 | 76.0554 | 75.0294 | 74.2864 | 73.1364 | 71.8934 | 70.8194 | 70.2014 | 69.2074 | 66.8904 | 63.7254 | 62.0404 | 60.6014 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WEST MELTON | 66 | 132 | West Melton | WEST MELTON SECTION 3 | S63 6EZ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WHINMOOR | 33 | 132 | Whinmoor | FERRYBRIDGE B | LS14 2DG | NZE (DFES Best View Scenario) | 113.0483 | 111.5673 | 109.3763 | 108.4603 | 107.8833 | 106.8723 | 105.7513 | 104.8103 | 104.3743 | 103.5183 | 101.9553 | 99.1883 | 97.7693 | 96.5673 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WOLD NEWTON | 33 | 132 | Wold Newton | KEADBY | DN37 0SW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4JJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BSP | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | ACKLAM | 11 | 33 | Bowesfield | NORTON | TS5 7LD | NZE (DFES Best View Scenario) | 15.5764 | 15.3524 | 15.1024 | 14.8324 | 14.5304 | 14.2084 | 13.8974 | 13.5964 | 13.2994 | 13.0094 | 11.8444 | 11.0114 | 10.5404 | 10.1404 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | AMBERTON ROAD | 11 | 66 | Hartmoor | HARTMOOR | TS24 8PQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | ANNFIELD 66/20KV | 20 | 66 | Annfield | STELLA SOUTH | DH9 7XW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | ASHINGTON | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE63 8UJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE FORREST | 11 | 33 | Darlington North | NORTON | DL1 3NL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | Darlington North | NORTON | DL5 6HY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BARDEN FRIAR | 20 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5JR | NZE (DFES Best View Scenario) | 7.577 | 7.563 | 7.546 | 7.529 | 7.509 | 7.488 | 7.467 | 7.446 | 7.425 | 7.405 | 7.318 | 7.252 | 7.209 | 7.17 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BEDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 1AH | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BELMONT | 11 | 66 | Potter House | SPENNYMOOR | DH1 2HL | NZE (DFES Best View Scenario) | 2.6535 | 2.4675 | 2.2595 | 2.0355 | 1.7845 | 1.5165 | 1.2555 | 1.0015 | 0.75051 | 0.50151 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BENSHAM | 11 | 66 | Dunston | STELLA NORTH | NE8 2XY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.479 | 11.304 | 11.132 | 10.443 | 9.949 | 9.667 | 9.427 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BENTON SQUARE | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE12 9SR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BENWELL | 11 | 66 | Dunston | STELLA NORTH | NE4 8XQ | NZE (DFES Best View Scenario) | 11.975 | 11.806 | 11.617 | 11.413 | 11.186 | 10.943 | 10.708 | 10.481 | 10.258 | 10.039 | 9.16 | 8.531 | 8.175 | 7.872 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | North Tees | NORTON | TS23 2AL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BILLY MILL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE29 8LP | NZE (DFES Best View Scenario) | 17.2369 | 17.0859 | 16.9159 | 16.7339 | 16.5289 | 16.3119 | 16.1009 | 15.8969 | 15.6969 | 15.4999 | 14.7119 | 14.1479 | 13.8289 | 13.5579 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | NZE (DFES Best View Scenario) | 32.5432 | 32.4242 | 32.2912 | 32.1492 | 31.9892 | 31.8182 | 31.6522 | 31.4912 | 31.3322 | 31.1752 | 30.5392 | 30.0772 | 29.8052 | 29.5702 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | Ravensworth | STELLA SOUTH | DH3 1JH | NZE (DFES Best View Scenario) | 24.1952 | 24.1212 | 24.0392 | 23.9502 | 23.8512 | 23.7452 | 23.6422 | 23.5422 | 23.4442 | 23.3482 | 22.9572 | 22.6762 | 22.5132 | 22.3732 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BLAYDON BURN | 11 | 66 | Dunston | STELLA NORTH | NE21 4BG | NZE (DFES Best View Scenario) | 1.8 | 1.635 | 1.451 | 1.253 | 1.031 | 0.794 | 0.565 | 0.343 | 0.125 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BLUCHER 33/11KV | 11 | 33 | Blucher | STELLA NORTH | NE15 9SB | NZE (DFES Best View Scenario) | 14.3812 | 14.2222 | 14.0442 | 13.8522 | 13.6372 | 13.4082 | 13.1872 | 12.9732 | 12.7622 | 12.5562 | 11.7262 | 11.1332 | 10.7972 | 10.5122 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BOLDON DOWNHILL | 20 | 66 | West Boldon | WEST BOLDON | NE36 0AS | NZE (DFES Best View Scenario) | 19.2055 | 19.0795 | 18.9385 | 18.7865 | 18.6165 | 18.4355 | 18.2595 | 18.0905 | 17.9235 | 17.7595 | 17.1025 | 16.6325 | 16.3655 | 16.1395 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BOROUGHBRIDGE/ROECLIFFE INDUSTRIAL | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | YO51 9NS | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 33/11KV | 11 | 33 | Bowesfield | NORTON | TS18 3HR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BOWESFIELD 66/11KV | 11 | 66 | North Tees | NORTON | TS23 1PX | NZE (DFES Best View Scenario) | 39.2181 | 39.1141 | 38.9981 | 38.8731 | 38.7341 | 38.5851 | 38.4411 | 38.3011 | 38.1641 | 38.0291 | 37.4861 | 37.0971 | 36.8741 | 36.6841 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BRANCEPETH | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL15 0TW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BREAMISH STREET | 11 | 66 | West Boldon | WEST BOLDON | NE1 2BL | NZE (DFES Best View Scenario) | 22.399 | 22.325 | 22.243 | 22.155 | 22.056 | 21.95 | 21.848 | 21.75 | 21.653 | 21.557 | 21.175 | 20.902 | 20.748 | 20.617 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | BRENDA TRADING | 11 | 66 | Hartmoor | HARTMOOR | TS25 1PD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CAMPLESHON ROAD | 11 | 33 | Melrosegate | OSBALDWICK | YO23 1HZ | NZE (DFES Best View Scenario) | 0.2627 | 0.086703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CARLEY HILL | 11 | 66 | West Boldon | WEST BOLDON | SR5 1SG | NZE (DFES Best View Scenario) | 19.386 | 19.181 | 18.951 | 18.704 | 18.427 | 18.131 | 17.846 | 17.57 | 17.298 | 17.031 | 15.961 | 15.196 | 14.762 | 14.394 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CARLIN HOW T3 T4 | 11 | 66 | Lackenby | LACKENBY | TS13 4DL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CARR HILL | 11 | 66 | West Boldon | WEST BOLDON | NE10 9SY | NZE (DFES Best View Scenario) | 19.8009 | 19.5639 | 19.2989 | 19.0129 | 18.6939 | 18.3529 | 18.0229 | 17.7039 | 17.3899 | 17.0819 | 15.8429 | 14.9559 | 14.4499 | 14.0189 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CATTERICK CAMP | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL9 3HE | NZE (DFES Best View Scenario) | 8.386 | 8.108 | 7.797 | 7.462 | 7.085 | 6.68 | 6.281 | 5.886 | 5.485 | 5.08 | 3.364 | 2.039 | 1.146 | 0.325 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CLOSE | 11 | 66 | Dunston | STELLA NORTH | NE1 3NB | NZE (DFES Best View Scenario) | 12.689 | 12.603 | 12.506 | 12.402 | 12.285 | 12.161 | 12.04 | 11.924 | 11.809 | 11.697 | 11.247 | 10.926 | 10.744 | 10.59 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CONEYTHORPE | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG5 0RZ | NZE (DFES Best View Scenario) | 6.7206 | 6.5876 | 6.4386 | 6.2786 | 6.0996 | 5.9076 | 5.7206 | 5.5376 | 5.3546 | 5.1736 | 4.4296 | 3.8776 | 3.5376 | 3.2366 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CONSETT | 20 | 66 | Annfield | STELLA SOUTH | DH8 7ND | NZE (DFES Best View Scenario) | 7.482 | 7.192 | 6.867 | 6.518 | 6.126 | 5.707 | 5.3 | 4.903 | 4.509 | 4.119 | 2.525 | 1.356 | 0.65 | 0.031 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CORPORATION STREET | 11 | 33 | Barrack Road | STELLA NORTH | NE4 5SS | NZE (DFES Best View Scenario) | 19.5255 | 19.4695 | 19.4065 | 19.3395 | 19.2635 | 19.1825 | 19.1045 | 19.0285 | 18.9545 | 18.8815 | 18.5895 | 18.3805 | 18.2615 | 18.1615 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | COWTON | 11 | 33 | Darlington Central | NORTON | DL6 2NF | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | Blyth 66kV | BLYTH 66KV | NE23 8AJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DARLEY | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG3 2PP | NZE (DFES Best View Scenario) | 9.455 | 9.394 | 9.327 | 9.254 | 9.173 | 9.086 | 9.001 | 8.919 | 8.836 | 8.755 | 8.42 | 8.174 | 8.023 | 7.89 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 132/6KV | 6 | 132 | Darlington 132/6kV | NORTON | DL1 1SW | NZE (DFES Best View Scenario) | 0 | 29.6274 | 29.5354 | 29.4354 | 29.3234 | 29.2044 | 29.0884 | 28.9764 | 28.8664 | 28.7574 | 28.3184 | 28.0014 | 27.8174 | 27.6594 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1SW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | Darlington Central | NORTON | DL1 1HG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON EAST | 11 | 33 | Darlington Central | NORTON | DL1 4NP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DARLINGTON WEST | 11 | 33 | Darlington North | NORTON | DL3 9QG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DENWICK | 20 | 66 | Linton | BLYTH 132kV | NE66 3RG | NZE (DFES Best View Scenario) | 5.631 | 5.308 | 4.946 | 4.557 | 4.119 | 3.65 | 3.191 | 2.739 | 2.285 | 1.83 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/11KV | 11 | 66 | Dunston | STELLA NORTH | NE11 9DH | NZE (DFES Best View Scenario) | 1.2713 | 1.1723 | 1.0623 | 0.94328 | 0.81028 | 0.66928 | 0.53128 | 0.39928 | 0.26828 | 0.14028 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DUNSTON 66/20KV | 20 | 66 | Dunston | STELLA NORTH | NE11 9DH | NZE (DFES Best View Scenario) | 11.84 | 11.661 | 11.462 | 11.246 | 11.005 | 10.749 | 10.5 | 10.26 | 10.023 | 9.79 | 8.857 | 8.188 | 7.806 | 7.482 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | DURHAM EAST | 11 | 66 | Potter House | SPENNYMOOR | DH1 5SU | NZE (DFES Best View Scenario) | 22.0228 | 21.9318 | 21.8308 | 21.7228 | 21.6008 | 21.4708 | 21.3448 | 21.2228 | 21.1018 | 20.9818 | 20.4968 | 20.1448 | 19.9378 | 19.7578 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | EASTFIELD | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 3BY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.8449 | 20.6029 | 20.3629 | 19.3729 | 18.6389 | 18.1839 | 17.7799 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | EASTGATE CEMENT | 20 | 66 | Toronto | SPENNYMOOR | DL13 2LA | NZE (DFES Best View Scenario) | 11.597 | 11.539 | 11.475 | 11.405 | 11.327 | 11.244 | 11.163 | 11.084 | 11.006 | 10.929 | 10.617 | 10.389 | 10.253 | 10.136 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | Barrack Road | STELLA NORTH | NE5 4JQ | NZE (DFES Best View Scenario) | 22.6249 | 22.5299 | 22.4239 | 22.3099 | 22.1829 | 22.0469 | 21.9149 | 21.7879 | 21.6619 | 21.5399 | 21.0469 | 20.6949 | 20.4949 | 20.3259 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | ELVINGTON | 11 | 33 | Melrosegate | OSBALDWICK | YO41 4DY | NZE (DFES Best View Scenario) | 0.9047 | 0.8627 | 0.8147 | 0.7627 | 0.7047 | 0.6427 | 0.5827 | 0.5247 | 0.4667 | 0.4097 | 0.1767 | 0.0077027 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | FARADAY STREET | 11 | 66 | North Tees | NORTON | TS1 4JG | NZE (DFES Best View Scenario) | 12.9988 | 12.7778 | 12.5308 | 12.2648 | 11.9668 | 11.6488 | 11.3418 | 11.0458 | 10.7528 | 10.4668 | 9.3178 | 8.4978 | 8.0328 | 7.6388 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | FAWDON T1 & SEATON BURN T1 | 20 | 66 | Blyth 66kV | BLYTH 66KV | NE3 2SW and NE13 6BH | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | FISHBURN | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | TS29 6JQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | FLATWORTH CENTRAL | 11 | 33 | Flatworth | TYNEMOUTH | NE29 7SH | NZE (DFES Best View Scenario) | 30.5997 | 30.5057 | 30.4007 | 30.2877 | 30.1607 | 30.0257 | 29.8957 | 29.7687 | 29.6447 | 29.5227 | 29.0347 | 28.6857 | 28.4877 | 28.3197 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | FOSS ISLANDS | 11 | 33 | Melrosegate | OSBALDWICK | YO31 7US | NZE (DFES Best View Scenario) | 1.1597 | 0.9447 | 0.7037 | 0.4437 | 0.1527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | FOSSWAY 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE6 4AN | NZE (DFES Best View Scenario) | 14.2139 | 14.0219 | 13.8079 | 13.5769 | 13.3179 | 13.0429 | 12.7759 | 12.5179 | 12.2649 | 12.0159 | 11.0179 | 10.3049 | 9.8999 | 9.5569 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | FYLANDS BRIDGE | 11 | 66 | Toronto | SPENNYMOOR | DL14 9TA | NZE (DFES Best View Scenario) | 9.77 | 9.546 | 9.296 | 9.026 | 8.723 | 8.4 | 8.086 | 7.78 | 7.476 | 7.176 | 5.951 | 5.055 | 4.515 | 4.044 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | GALE LANE | 11 | 33 | Poppleton | POPPLETON | YO24 3AF | NZE (DFES Best View Scenario) | 7.618 | 7.449 | 7.261 | 7.059 | 6.832 | 6.59 | 6.356 | 6.129 | 5.905 | 5.685 | 4.797 | 4.158 | 3.79 | 3.474 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | GARWOOD STREET | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 5DQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.2046 | 19.9736 | 19.7466 | 18.8356 | 18.1846 | 17.8156 | 17.5036 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD CENTRAL | 11 | 33 | Barrack Road | STELLA NORTH | NE8 1HB | NZE (DFES Best View Scenario) | 16.8398 | 16.7588 | 16.6668 | 16.5688 | 16.4588 | 16.3408 | 16.2268 | 16.1168 | 16.0088 | 15.9028 | 15.4758 | 15.1708 | 14.9968 | 14.8498 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | GATESHEAD EAST | 11 | 66 | West Boldon | WEST BOLDON | NE8 3AH | NZE (DFES Best View Scenario) | 22.609 | 22.595 | 22.58 | 22.564 | 22.546 | 22.527 | 22.509 | 22.491 | 22.473 | 22.456 | 22.387 | 22.337 | 22.309 | 22.285 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | GOSFORTH 33/11KV | 11 | 33 | Gosforth | TYNEMOUTH | NE3 1RR | NZE (DFES Best View Scenario) | 30.439 | 30.366 | 30.285 | 30.197 | 30.099 | 29.995 | 29.894 | 29.796 | 29.7 | 29.605 | 29.226 | 28.956 | 28.802 | 28.672 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | GRANGETOWN | 11 | 66 | Lackenby | LACKENBY | TS6 7AS | NZE (DFES Best View Scenario) | 11.2849 | 11.0739 | 10.8379 | 10.5849 | 10.3009 | 9.9979 | 9.7039 | 9.4199 | 9.1389 | 8.8639 | 7.7519 | 6.9509 | 6.4889 | 6.0929 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | GREATHAM | 11 | 132 | Greatham | SALTHOLME | TS25 2DD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | Lackenby | LACKENBY | TS14 6GQ | NZE (DFES Best View Scenario) | 5.618 | 5.334 | 5.015 | 4.672 | 4.288 | 3.877 | 3.478 | 3.09 | 2.706 | 2.327 | 0.78402 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HARLOW GREEN | 11 | 66 | West Boldon | WEST BOLDON | NE9 6NT | NZE (DFES Best View Scenario) | 14.2541 | 14.0491 | 13.8191 | 13.5721 | 13.2961 | 13.0011 | 12.7161 | 12.4401 | 12.1681 | 11.9011 | 10.8301 | 10.0621 | 9.6241 | 9.2521 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HARMIRE BRIDGE | 20 | 66 | Toronto | SPENNYMOOR | DL12 8QJ | NZE (DFES Best View Scenario) | 8.182 | 8.02 | 7.838 | 7.642 | 7.423 | 7.189 | 6.961 | 6.739 | 6.518 | 6.3 | 5.409 | 4.755 | 4.36 | 4.014 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HARRATON | 11 | 132 | Harraton | STELLA SOUTH | NE38 9BZ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.391 | 36.207 | 36.026 | 35.298 | 34.779 | 34.484 | 34.234 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE 132/11KV | 11 | 132 | Harrogate 132/11kV | KNARESBOROUGH | HG1 2BN | NZE (DFES Best View Scenario) | 27.332 | 26.967 | 26.558 | 26.118 | 25.625 | 25.097 | 24.583 | 24.081 | 23.58 | 23.083 | 21.036 | 19.521 | 18.585 | 17.756 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HARROGATE WEST | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 0QB | NZE (DFES Best View Scenario) | 32.497 | 32.402 | 32.295 | 32.181 | 32.052 | 31.915 | 31.781 | 31.65 | 31.52 | 31.39 | 30.859 | 30.467 | 30.226 | 30.013 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HARTMOOR 66/20KV | 20 | 66 | Hartmoor | HARTMOOR | TS27 3BL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HAWTHORN PIT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 9NX | NZE (DFES Best View Scenario) | 10.189 | 9.9 | 9.577 | 9.229 | 8.839 | 8.422 | 8.018 | 7.626 | 7.238 | 6.856 | 5.304 | 4.179 | 3.516 | 2.943 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | Melrosegate | OSBALDWICK | YO31 8FZ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN | 6 | 66 | West Boldon | WEST BOLDON | NE31 1BD | NZE (DFES Best View Scenario) | 0 | 4.8068 | 4.7628 | 4.7148 | 4.6628 | 4.6058 | 4.5518 | 4.4988 | 4.4468 | 4.3958 | 4.1918 | 4.0468 | 3.9638 | 3.8938 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HEBBURN WEST | 11 | 66 | West Boldon | WEST BOLDON | NE31 1NA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HEDWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE32 4SW | NZE (DFES Best View Scenario) | 0.27929 | 0.15829 | 0.02329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HEIGHINGTON | 11 | 33 | Darlington North | NORTON | DL5 6JW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HEXHAM | 20 | 66 | Coalburns | STELLA SOUTH | NE46 4NT | NZE (DFES Best View Scenario) | 27.8779 | 27.7259 | 27.5569 | 27.3739 | 27.1689 | 26.9489 | 26.7339 | 26.5209 | 26.3069 | 26.0929 | 25.1939 | 24.5109 | 24.0649 | 23.6609 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HIGH BARMSTON | 11 | 66 | West Boldon | WEST BOLDON | NE38 8QA | NZE (DFES Best View Scenario) | 20.626 | 20.487 | 20.33 | 20.162 | 19.973 | 19.772 | 19.578 | 19.39 | 19.205 | 19.024 | 18.295 | 17.775 | 17.479 | 17.229 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HIGH FLATTS | 11 | 66 | Potter House | SPENNYMOOR | DH2 2LR | NZE (DFES Best View Scenario) | 21.1712 | 20.9512 | 20.7052 | 20.4412 | 20.1442 | 19.8272 | 19.5182 | 19.2182 | 18.9212 | 18.6262 | 17.4262 | 16.5482 | 16.0202 | 15.5602 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HOUGHTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | DH4 5HP | NZE (DFES Best View Scenario) | 3.6651 | 3.4801 | 3.2731 | 3.0491 | 2.8001 | 2.5331 | 2.2741 | 2.0241 | 1.7761 | 1.5331 | 0.54714 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HOWDON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 0JX | NZE (DFES Best View Scenario) | 4.3075 | 4.2575 | 4.2015 | 4.1415 | 4.0745 | 4.0035 | 3.9345 | 3.8675 | 3.8015 | 3.7375 | 3.4785 | 3.2935 | 3.1885 | 3.0995 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HUNTINGTON NEW LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO32 9TA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | Husthwaite | KNARESBOROUGH | YO61 4PN | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | JARROW | 11 | 33 | South Shields | SOUTH SHIELDS | NE32 5LD | NZE (DFES Best View Scenario) | 18.3816 | 18.3386 | 18.2916 | 18.2396 | 18.1826 | 18.1216 | 18.0626 | 18.0056 | 17.9496 | 17.8946 | 17.6736 | 17.5156 | 17.4256 | 17.3496 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | KENTON | 11 | 33 | Blucher | STELLA NORTH | NE3 4UP | NZE (DFES Best View Scenario) | 3.0931 | 2.9601 | 2.8111 | 2.6501 | 2.4711 | 2.2791 | 2.0941 | 1.9141 | 1.7381 | 1.5651 | 0.8711 | 0.3751 | 0.093103 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | KIELDER | 20 | 33 | Spadeadam 33kV | SPADEADAM | NE48 1BH | NZE (DFES Best View Scenario) | 4.041 | 4.026 | 4.008 | 3.99 | 3.969 | 3.947 | 3.926 | 3.904 | 3.883 | 3.862 | 3.774 | 3.708 | 3.667 | 3.63 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | KILLINGWORTH | 11 | 33 | Gosforth | TYNEMOUTH | NE12 6QQ | NZE (DFES Best View Scenario) | 11.493 | 11.371 | 11.234 | 11.087 | 10.922 | 10.747 | 10.577 | 10.413 | 10.252 | 10.093 | 9.458 | 9.004 | 8.746 | 8.528 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | KIRBYMOORSIDE | 11 | 66 | Malton Grid | OSBALDWICK | YO62 6EZ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | LINTON 66/20KV | 20 | 66 | Linton | BLYTH 132kV | NE61 3AX | NZE (DFES Best View Scenario) | 7.271 | 7.145 | 7.004 | 6.852 | 6.681 | 6.498 | 6.318 | 6.141 | 5.962 | 5.782 | 5.028 | 4.454 | 4.076 | 3.732 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | LONGBENTON | 11 | 33 | Gosforth | TYNEMOUTH | NE7 7LR | NZE (DFES Best View Scenario) | 19.4522 | 19.2962 | 19.1212 | 18.9342 | 18.7232 | 18.4992 | 18.2822 | 18.0722 | 17.8662 | 17.6642 | 16.8522 | 16.2712 | 15.9422 | 15.6632 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | LOW SPENNYMOOR | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL16 7RS | NZE (DFES Best View Scenario) | 7.91 | 7.78 | 7.633 | 7.475 | 7.299 | 7.11 | 6.926 | 6.747 | 6.57 | 6.394 | 5.678 | 5.154 | 4.838 | 4.562 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | LYNEMOUTH | 20 | 66 | Linton | BLYTH 132kV | NE61 5XH | NZE (DFES Best View Scenario) | 6.051 | 6.02 | 5.986 | 5.948 | 5.907 | 5.862 | 5.818 | 5.774 | 5.73 | 5.686 | 5.499 | 5.357 | 5.263 | 5.177 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MADDISON STREET | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE24 1HD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MALLEABLE | 11 | 66 | North Tees | NORTON | TS18 2NR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1759 | 0.99788 | 0.82388 | 0.12188 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MALTON | 11 | 66 | Malton Grid | OSBALDWICK | YO17 6BT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MEADOWFIELD | 11 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH7 8ER | NZE (DFES Best View Scenario) | 0.835 | 0.763 | 0.682 | 0.595 | 0.497 | 0.393 | 0.291 | 0.192 | 0.095 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MELROSEGATE 33/11KV | 11 | 33 | Melrosegate | OSBALDWICK | YO31 0YB | NZE (DFES Best View Scenario) | 1.5847 | 1.4807 | 1.3647 | 1.2397 | 1.0987 | 0.9497 | 0.8047 | 0.6647 | 0.5267 | 0.3907 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MILLBANK LANE | 11 | 33 | Bowesfield | NORTON | TS17 0AX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5382 | 18.3022 | 18.0712 | 17.1372 | 16.4672 | 16.0822 | 15.7532 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MONKSEATON | 11 | 33 | Chirton Grange | TYNEMOUTH | NE25 9AF | NZE (DFES Best View Scenario) | 19.2352 | 18.9952 | 18.7262 | 18.4362 | 18.1112 | 17.7642 | 36.667 | 36.341 | 36.018 | 35.7 | 34.411 | 33.477 | 32.927 | 32.453 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MOOR MONKTON PUMPS | 11 | 33 | Poppleton | POPPLETON | YO30 1BY | NZE (DFES Best View Scenario) | 13.3899 | 13.3659 | 13.3389 | 13.3109 | 13.2779 | 13.2439 | 13.2099 | 13.1779 | 13.1449 | 13.1119 | 12.9759 | 12.8749 | 12.8119 | 12.7549 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MORPETH | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE61 6JH | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | MOUNT ROAD | 11 | 33 | Offerton | OFFERTON | SR4 7LJ | NZE (DFES Best View Scenario) | 23.9282 | 23.7332 | 23.5132 | 23.2772 | 23.0132 | 22.7322 | 22.4592 | 22.1962 | 21.9372 | 21.6832 | 20.6632 | 19.9332 | 19.5202 | 19.1692 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | NEWBURN HAUGH | 11 | 132 | Newburn Haugh | STELLA NORTH | NE15 8SF | NZE (DFES Best View Scenario) | 20.4034 | 20.3454 | 20.2804 | 20.2104 | 20.1314 | 20.0484 | 19.9674 | 19.8894 | 19.8124 | 19.7374 | 19.4344 | 19.2184 | 19.0954 | 18.9914 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | NEWBY | 11 | 33 | Scarborough Grid | OSBALDWICK | YO12 6NL | NZE (DFES Best View Scenario) | 0.093868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | NEWCASTLE AIRPORT | 11 | 33 | Blucher | STELLA NORTH | NE13 8DF | NZE (DFES Best View Scenario) | 27.0453 | 26.9343 | 26.8113 | 26.6783 | 26.5283 | 26.3683 | 26.2123 | 26.0603 | 25.9073 | 25.7563 | 25.1313 | 24.6663 | 24.3763 | 24.1193 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | Darlington North | NORTON | DL5 6EA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | NORTH STREET | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 1DU | NZE (DFES Best View Scenario) | 1.2984 | 1.1614 | 1.0074 | 0.8424 | 0.6574 | 0.4604 | 0.2674 | 0.079403 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T1 T2 | 11 | 66 | North Tees | NORTON | TS23 1PX | NZE (DFES Best View Scenario) | 22.2844 | 22.2254 | 22.1594 | 22.0874 | 22.0074 | 21.9224 | 21.8404 | 21.7604 | 21.6824 | 21.6054 | 21.2974 | 21.0774 | 20.9524 | 20.8464 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | NORTH TEES T3 T4 | 11 | 66 | North Tees | NORTON | TS23 1PY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1537 | 8.0107 | 7.8697 | 7.3057 | 6.9017 | 6.6717 | 6.4767 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | NORTHALLERTON | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 0QE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | NORTON 132/11KV | 11 | 132 | Norton 132/11kV | NORTON | TS21 1EG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | OATLANDS | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 8BY | NZE (DFES Best View Scenario) | 18.1918 | 18.0578 | 17.9078 | 17.7468 | 17.5658 | 17.3718 | 17.1828 | 16.9988 | 16.8148 | 16.6318 | 15.8788 | 15.3198 | 14.9738 | 14.6668 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | OFFERTON 33/11KV | 11 | 33 | Offerton | OFFERTON | SR4 9NR | NZE (DFES Best View Scenario) | 26.4388 | 26.2448 | 26.0288 | 25.7958 | 25.5348 | 25.2568 | 24.9878 | 24.7268 | 24.4708 | 24.2188 | 23.2058 | 22.4788 | 22.0638 | 21.7108 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | PALLION TRADING | 11 | 33 | Offerton | OFFERTON | SR4 6SN | NZE (DFES Best View Scenario) | 13.4748 | 13.3098 | 13.1248 | 12.9248 | 12.7018 | 12.4638 | 12.2338 | 12.0118 | 11.7928 | 11.5778 | 10.7158 | 10.0998 | 9.7498 | 9.4538 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2HR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | PETERLEE WEST | 11 | 66 | Hartmoor | HARTMOOR | DH6 2RA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | PILGRIM | 11 | 33 | Barrack Road | STELLA NORTH | NE1 2LA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6142 | 3.5682 | 3.5222 | 3.3392 | 3.2092 | 3.1352 | 3.0722 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | Potter House | SPENNYMOOR | DH1 5FF | NZE (DFES Best View Scenario) | 4.326 | 4.086 | 3.817 | 3.528 | 3.204 | 2.858 | 2.522 | 2.194 | 1.868 | 1.547 | 0.23305 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | Potter House | SPENNYMOOR | DH1 5FF | NZE (DFES Best View Scenario) | 26.1972 | 26.1582 | 26.1152 | 26.0682 | 26.0152 | 25.9592 | 25.9052 | 25.8522 | 25.7992 | 25.7472 | 25.5362 | 25.3822 | 25.2912 | 25.2112 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | PRISSICK | 11 | 66 | Lackenby | LACKENBY | TS4 3SG | NZE (DFES Best View Scenario) | 21.3077 | 21.1017 | 20.8717 | 20.6237 | 20.3467 | 20.0507 | 19.7637 | 19.4877 | 19.2147 | 18.9487 | 17.8777 | 17.1117 | 16.6777 | 16.3107 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | RAVENSCAR | 11 | 33 | Scarborough Grid | OSBALDWICK | YO13 0LZ | NZE (DFES Best View Scenario) | 10.009 | 9.993 | 9.974 | 9.955 | 9.933 | 9.91 | 9.887 | 9.864 | 9.842 | 9.82 | 9.73 | 9.664 | 9.623 | 9.587 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | RAWCLIFFE LANE | 11 | 33 | Melrosegate | OSBALDWICK | YO30 5SW | NZE (DFES Best View Scenario) | 0.7367 | 0.5837 | 0.4127 | 0.2287 | 0.022703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | REDCAR | 11 | 66 | Lackenby | LACKENBY | TS10 2PA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | RESERVOIR | 20 | 66 | Blyth 66kV | BLYTH 66kV | NE22 5QP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T1 | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL10 5BJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | RICHMOND T2 | 11 | 33 | Darlington North | NORTON | DL10 5BJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | RIPON | 11 | 33 | Wormald Green 132/33kV | KNARESBOROUGH | HG4 1QE | NZE (DFES Best View Scenario) | 14.1929 | 13.9519 | 13.6829 | 17.35 | 17.025 | 16.678 | 16.339 | 16.008 | 15.679 | 15.352 | 14.008 | 13.014 | 12.402 | 11.862 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | RISE CARR | 6 | 33 | Darlington North | NORTON | DL3 0RP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | ROMANBY | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL7 8HP | NZE (DFES Best View Scenario) | 9.8931 | 9.7911 | 9.6761 | 9.5531 | 9.4151 | 9.2661 | 9.1211 | 8.9791 | 8.8361 | 8.6931 | 8.1001 | 7.6541 | 7.3691 | 7.1131 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | RUDBY | 11 | 33 | Bowesfield | NORTON | TS15 0JT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | Scarborough Grid | OSBALDWICK | YO11 2YH | NZE (DFES Best View Scenario) | 2.011 | 1.789 | 1.54 | 1.273 | 0.97402 | 0.65302 | 0.34102 | 0.035017 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SEGHILL | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 7EY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SESSAY BRIDGE_SOWERBY | 11 | 33 | Husthwaite | KNARESBOROUGH | YO7 3NT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SEVERUS HILL | 11 | 33 | Poppleton | POPPLETON | YO26 4RR | NZE (DFES Best View Scenario) | 0.65757 | 0.51457 | 0.35557 | 0.18357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SHERIFF HUTTON | 11 | 66 | Malton Grid | OSBALDWICK | YO60 6QN | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SHOTTON | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR8 2EL | NZE (DFES Best View Scenario) | 1.2332 | 1.0832 | 0.91517 | 0.73417 | 0.53117 | 0.31417 | 0.10317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SIMONSIDE | 11 | 33 | South Shields | SOUTH SHIELDS | NE34 9PD | NZE (DFES Best View Scenario) | 13.1151 | 12.9981 | 12.8681 | 12.7271 | 12.5691 | 12.4021 | 12.2391 | 12.0821 | 11.9281 | 11.7761 | 11.1691 | 10.7341 | 10.4881 | 10.2791 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SKELDERGATE | 11 | 33 | Poppleton | POPPLETON | YO1 6HN | NZE (DFES Best View Scenario) | 2.0349 | 1.9509 | 1.8579 | 1.7579 | 1.6459 | 1.5259 | 1.4099 | 1.2969 | 1.1869 | 1.0779 | 0.64088 | 0.32688 | 0.14688 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SKERNESIDE | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DL5 6JH | NZE (DFES Best View Scenario) | 0.13562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SPENCERBECK | 11 | 66 | Lackenby | LACKENBY | TS3 8TE | NZE (DFES Best View Scenario) | 34.3736 | 34.1246 | 33.8466 | 33.5466 | 33.2106 | 32.8526 | 32.5066 | 32.1716 | 31.8416 | 31.5176 | 30.2156 | 29.2826 | 28.7496 | 28.2956 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | Spennymoor 132/66kV | SPENNYMOOR | DH6 5JX | NZE (DFES Best View Scenario) | 0.56567 | 0.37167 | 0.15467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | STARBECK | 11 | 33 | Harrogate 132/33kV | KNARESBOROUGH | HG2 7PT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | STOKESLEY | 11 | 33 | Bowesfield | NORTON | TS9 5HS | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | STONEY CUT | 20 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR7 8RQ | NZE (DFES Best View Scenario) | 15.7262 | 15.5352 | 15.3222 | 15.0932 | 14.8352 | 14.5602 | 14.2932 | 14.0332 | 13.7752 | 13.5202 | 12.4782 | 11.7162 | 11.2572 | 10.8572 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T1 T2 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | NZE (DFES Best View Scenario) | 20.8893 | 20.7353 | 20.5633 | 20.3783 | 20.1713 | 19.9503 | 19.7373 | 19.5303 | 19.3273 | 19.1283 | 18.3283 | 17.7563 | 17.4333 | 17.1583 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | SUNDERLAND T5 T6 | 11 | 66 | West Boldon | WEST BOLDON | SR4 6BU | NZE (DFES Best View Scenario) | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.799 | 22.799 | 22.799 | 22.799 | 22.799 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | TANFIELD | 11 | 66 | Annfield | STELLA SOUTH | DH9 9DB | NZE (DFES Best View Scenario) | 0.45115 | 0.27515 | 0.07815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | TEAM VALLEY | 20 | 66 | Ravensworth | STELLA SOUTH | NE11 0SX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.8301 | 44.7371 | 44.6451 | 44.2791 | 44.0161 | 43.8671 | 43.7411 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | Seal Sands | SALTHOLME | TS23 3NF | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | TEMPLE PARK | 11 | 66 | West Boldon | WEST BOLDON | NE34 8TH | NZE (DFES Best View Scenario) | 19.9194 | 19.7244 | 19.5054 | 19.2694 | 19.0054 | 18.7244 | 18.4524 | 18.1894 | 17.9304 | 17.6764 | 16.6574 | 15.9284 | 15.5154 | 15.1654 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | THIRSK | 11 | 33 | Leeming Bar_Skeeby | NORTON | YO7 4NH | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | THORNTON DALE | 11 | 66 | Malton Grid | OSBALDWICK | YO18 7SJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | TORONTO 66/20KV | 20 | 66 | Toronto | SPENNYMOOR | DL14 7RJ | NZE (DFES Best View Scenario) | 7.96 | 7.731 | 7.474 | 7.198 | 6.888 | 6.557 | 6.236 | 5.923 | 5.613 | 5.307 | 4.059 | 3.147 | 2.602 | 2.126 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | TUNSTALL | 11 | 66 | Hawthorn Pit Grid | HAWTHORN PIT GRID | SR3 2BT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.1129 | 24.8039 | 24.4999 | 23.2819 | 22.4109 | 21.9159 | 21.4959 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | Chirton Grange | TYNEMOUTH | NE30 1JG | NZE (DFES Best View Scenario) | 19.5435 | 19.3465 | 19.1265 | 18.8895 | 18.6245 | 18.3415 | 18.0675 | 17.8035 | 17.5435 | 17.2885 | 16.2645 | 15.5335 | 15.1195 | 14.7685 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | UNIVERSITY | 11 | 33 | Barrack Road | STELLA NORTH | NE2 4PZ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3957 | 10.3367 | 10.2787 | 10.0447 | 9.8777 | 9.7827 | 9.7027 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | URLAY NOOK | 11 | 33 | Bowesfield | NORTON | TS16 0QB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | USWORTH | 11 | 66 | West Boldon | WEST BOLDON | NE37 3HY | NZE (DFES Best View Scenario) | 21.547 | 21.466 | 21.375 | 21.277 | 21.167 | 21.05 | 20.937 | 20.828 | 20.72 | 20.615 | 20.191 | 19.888 | 19.716 | 19.57 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WALKER | 11 | 66 | West Boldon | WEST BOLDON | NE6 3PZ | NZE (DFES Best View Scenario) | 14.4789 | 14.3079 | 14.1159 | 13.9089 | 13.6779 | 13.4309 | 13.1919 | 12.9609 | 12.7339 | 12.5119 | 11.6179 | 10.9789 | 10.6169 | 10.3089 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WANSBECK | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE22 7DH | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WARDLEY | 6 | 66 | West Boldon | WEST BOLDON | NE31 1LP | NZE (DFES Best View Scenario) | 0 | 15.5924 | 15.4844 | 15.3674 | 15.2374 | 15.0984 | 14.9644 | 14.8344 | 14.7064 | 14.5814 | 14.0774 | 13.7164 | 13.5114 | 13.3374 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WARKWORTH | 20 | 66 | Linton | BLYTH 132kV | NE65 0YD | NZE (DFES Best View Scenario) | 6.201 | 5.951 | 5.671 | 5.37 | 5.031 | 4.668 | 4.312 | 3.961 | 3.607 | 3.253 | 1.769 | 0.643 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WENSLEYDALE | 11 | 33 | Leeming Bar_Skeeby | NORTON | DL8 5ED | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WEST HARTFORD | 11 | 66 | Blyth 66kV | BLYTH 66kV | NE23 3JP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WEST SOUTHWICK | 11 | 66 | West Boldon | WEST BOLDON | SR5 3TX | NZE (DFES Best View Scenario) | 20.565 | 20.463 | 20.349 | 20.226 | 20.089 | 19.942 | 19.8 | 19.663 | 19.528 | 19.396 | 18.865 | 18.485 | 18.269 | 18.086 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WEST WYLAM | 20 | 66 | Coalburns | STELLA SOUTH | NE42 5EX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WESTERHOPE | 11 | 33 | Blucher | STELLA NORTH | NE5 5HH | NZE (DFES Best View Scenario) | 18.9463 | 18.8033 | 18.6423 | 18.4693 | 18.2753 | 18.0693 | 17.8693 | 17.6763 | 17.4853 | 17.2993 | 16.5513 | 16.0153 | 15.7123 | 15.4543 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WESTOE | 11 | 33 | South Shields | SOUTH SHIELDS | NE33 3GE | NZE (DFES Best View Scenario) | 13.045 | 12.891 | 12.718 | 12.531 | 12.323 | 12.1 | 11.885 | 11.677 | 11.472 | 11.272 | 10.466 | 9.891 | 9.564 | 9.288 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO22 4JE | NZE (DFES Best View Scenario) | 11.7531 | 11.7091 | 11.6591 | 11.6051 | 11.5451 | 11.4801 | 11.4171 | 11.3561 | 11.2951 | 11.2341 | 10.9851 | 10.8011 | 10.6891 | 10.5891 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO22 4JE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T1 | 11 | 33 | Scarborough Grid | OSBALDWICK | YO21 1LY | NZE (DFES Best View Scenario) | 11.6689 | 11.6139 | 11.5519 | 11.4859 | 11.4109 | 11.3319 | 11.2539 | 11.1789 | 11.1029 | 11.0279 | 10.7199 | 10.4919 | 10.3519 | 10.2279 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WHITBY WEST T2 | 11 | 66 | Malton Grid | OSBALDWICK | YO21 1LY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WILLINGTON | 11 | 33 | Flatworth | TYNEMOUTH | NE28 7HS | NZE (DFES Best View Scenario) | 18.4272 | 18.2722 | 18.0982 | 17.9112 | 17.7022 | 17.4782 | 17.2632 | 17.0542 | 16.8492 | 16.6482 | 15.8402 | 15.2622 | 14.9352 | 14.6582 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | Wormald Green 132/11kV | KNARESBOROUGH | HG3 3PS | NZE (DFES Best View Scenario) | 13.047 | 12.935 | 12.809 | 12.673 | 12.52 | 12.357 | 12.199 | 12.043 | 11.889 | 11.735 | 11.104 | 10.637 | 10.348 | 10.093 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | WYNYARD | 11 | 66 | Hartmoor | HARTMOOR | TS2 2FB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | YEDINGHAM | 11 | 66 | Malton Grid | OSBALDWICK | YO17 8RR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgN | YORK UNIVERSITY | 11 | 33 | Melrosegate | OSBALDWICK | YO10 5ZF | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ABBEY ROAD | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS5 3NF | NZE (DFES Best View Scenario) | 1.7903 | 1.7023 | 1.6043 | 1.4993 | 1.3823 | 1.2563 | 1.1353 | 1.0163 | 0.89933 | 0.78333 | 0.31133 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | AIREDALE ROAD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 4LJ | NZE (DFES Best View Scenario) | 13.0276 | 12.9636 | 12.8936 | 12.8176 | 12.7326 | 12.6416 | 12.5536 | 12.4676 | 12.3826 | 12.2986 | 11.9566 | 11.7066 | 11.5566 | 11.4266 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ALDHAM | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S73 8SW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ALFRED GELDER STREET | 11 | 33 | Hull South | CREYKE BECK | HU1 1EP | NZE (DFES Best View Scenario) | 2.8489 | 2.8149 | 2.7769 | 2.7359 | 2.6909 | 2.6419 | 2.5949 | 2.5489 | 2.5039 | 2.4599 | 2.2829 | 2.1569 | 2.0839 | 2.0229 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T1 | 11 | 33 | Leeds East | SKELTON GRANGE | LS7 3QB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ALLERTON HILL T2 | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 3QB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ALVERTHORPE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 9PB | NZE (DFES Best View Scenario) | 21.5313 | 21.3533 | 21.1553 | 20.9413 | 20.7023 | 20.4483 | 20.2003 | 19.9593 | 19.7203 | 19.4843 | 18.5213 | 17.8163 | 17.3923 | 17.0233 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ARMOURIES DRIVE | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LT | NZE (DFES Best View Scenario) | 7.079 | 7.038 | 6.992 | 6.943 | 6.888 | 6.829 | 6.772 | 6.717 | 6.662 | 6.608 | 6.387 | 6.226 | 6.13 | 6.046 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ARMTHORPE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3DY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ARUNDEL STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4PJ | NZE (DFES Best View Scenario) | 4.4168 | 4.3948 | 4.3708 | 4.3458 | 4.3168 | 4.2858 | 4.2558 | 4.2268 | 4.1978 | 4.1688 | 4.0528 | 3.9688 | 3.9178 | 3.8738 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ASKERN | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN6 0BY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | AUDBY LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 7SU | NZE (DFES Best View Scenario) | 3.4264 | 3.2704 | 3.0964 | 2.9084 | 2.6994 | 2.4764 | 2.2594 | 2.0464 | 1.8354 | 1.6254 | 0.76538 | 0.13138 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | AUSTERFIELD | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN10 6HD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BAILIFF BRIDGE | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 4DT | NZE (DFES Best View Scenario) | 1.2325 | 1.1455 | 1.0485 | 0.94448 | 0.82848 | 0.70448 | 0.58248 | 0.46348 | 0.34348 | 0.22448 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BALBY | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN4 8DG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BALME STREET | 11 | 33 | Bradford | BRADFORD WEST | BD1 4BA | NZE (DFES Best View Scenario) | 3.2706 | 3.2076 | 3.1376 | 3.0626 | 2.9786 | 2.8886 | 2.8016 | 2.7166 | 2.6326 | 2.5496 | 2.2116 | 1.9636 | 1.8156 | 1.6866 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BARNBURGH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 9NT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BARNOLDSWICK | 11 | 33 | Silsden | BRADFORD WEST | BB18 5RU | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BARNSLEY ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 7AU | NZE (DFES Best View Scenario) | 32.1102 | 32.0492 | 31.9802 | 31.9072 | 31.8252 | 31.7372 | 31.6522 | 31.5692 | 31.4872 | 31.4062 | 31.0762 | 30.8352 | 30.6912 | 30.5662 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BARROW | 11 | 33 | Immingham | GRIMSBY WEST | DN19 7EG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BARUGH 66/11KV | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BARWICK | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS15 8SW | NZE (DFES Best View Scenario) | 13.0174 | 12.9024 | 12.7734 | 12.6344 | 12.4804 | 12.3144 | 12.1544 | 11.9984 | 11.8434 | 11.6914 | 11.0694 | 10.6154 | 10.3444 | 10.1094 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BASLOW ROAD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S17 3LT | NZE (DFES Best View Scenario) | 0.15292 | 0.058919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BATLEY | 11 | 33 | Thornhill 132kV | ELLAND | WF17 6HU | NZE (DFES Best View Scenario) | 4.7314 | 4.5754 | 4.4004 | 4.2134 | 4.0034 | 3.7804 | 3.5624 | 3.3504 | 3.1394 | 2.9304 | 2.0754 | 1.4464 | 1.0644 | 0.72942 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BEAL | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 8DT | NZE (DFES Best View Scenario) | 3.8351 | 3.7491 | 3.6551 | 3.5521 | 3.4401 | 3.3191 | 3.1991 | 3.0801 | 2.9601 | 2.8371 | 2.3181 | 1.9141 | 1.6391 | 1.3851 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | NZE (DFES Best View Scenario) | 8.5465 | 8.5115 | 8.4735 | 8.4315 | 8.3855 | 8.3365 | 8.2885 | 8.2415 | 8.1955 | 8.1495 | 7.9635 | 7.8285 | 7.7475 | 7.6775 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 6EY | NZE (DFES Best View Scenario) | 38.3592 | 38.2782 | 38.1862 | 38.0882 | 37.9792 | 37.8622 | 37.7482 | 37.6382 | 37.5282 | 37.4202 | 36.9802 | 36.6592 | 36.4682 | 36.3012 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BEIGHTON | 11 | 66 | Thurcroft | THURCROFT | S26 4TL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BELLHOUSE ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S5 0PL | NZE (DFES Best View Scenario) | 1.2067 | 1.0557 | 0.88773 | 0.70573 | 0.50373 | 0.28773 | 0.078728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT AVENUE | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN4 8DF | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BELMONT COVERT | 11 | 33 | Wold Newton | KEADBY | LN11 9RA | NZE (DFES Best View Scenario) | 0.0014624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BELTHORPE LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1SB | NZE (DFES Best View Scenario) | 12.312 | 12.283 | 12.251 | 12.216 | 12.178 | 12.136 | 12.095 | 12.055 | 12.013 | 11.97 | 11.788 | 11.644 | 11.544 | 11.451 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BENTLEY | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN5 0NG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BILLET LANE | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BINBROOK | 11 | 33 | Wold Newton | KEADBY | LN8 6DR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BINGLEY 33/11KV | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 2RD | NZE (DFES Best View Scenario) | 13.3126 | 13.1976 | 13.0686 | 12.9306 | 12.7766 | 12.6116 | 12.4516 | 12.2956 | 12.1406 | 11.9876 | 11.3636 | 10.9066 | 10.6326 | 10.3926 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BIRKBY | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 5HB | NZE (DFES Best View Scenario) | 0.18455 | 0.064548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1HF | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BLUE BOY STREET | 11 | 33 | Neepsend | NEEPSEND | S3 7BA | NZE (DFES Best View Scenario) | 1.341 | 1.318 | 1.291 | 1.263 | 1.231 | 1.198 | 1.165 | 1.133 | 1.102 | 1.07 | 0.94296 | 0.85096 | 0.79496 | 0.74696 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BOC BRINSWORTH | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1WT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BOLTON ROAD | 11 | 33 | Silsden | BRADFORD WEST | BD20 0JT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BOTTESFORD | 11 | 33 | Scunthorpe South | KEADBY | DN16 3UJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BRAMHOPE | 11 | 33 | Menston | BRADFORD WEST | LS16 9HA | NZE (DFES Best View Scenario) | 0.72911 | 0.70011 | 0.66811 | 0.63311 | 0.59511 | 0.55411 | 0.51411 | 0.47511 | 0.43711 | 0.39911 | 0.24411 | 0.13211 | 0.06411 | 0.0061098 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BRAMLEY | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS13 3ST | NZE (DFES Best View Scenario) | 21.5038 | 21.3448 | 21.1668 | 20.9748 | 20.7618 | 20.5328 | 20.3118 | 20.0958 | 19.8818 | 19.6708 | 18.8118 | 18.1848 | 17.8108 | 17.4858 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BRETT STREET | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 4HW | NZE (DFES Best View Scenario) | 16.8605 | 16.5155 | 16.1305 | 15.7165 | 15.2625 | 14.7715 | 14.2865 | 13.7995 | 13.3005 | 12.7935 | 10.6015 | 8.8725 | 7.6535 | 6.5145 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BRIDGES ROAD | 11 | 33 | Scunthorpe South | KEADBY | DN17 1HA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1QE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BRODSWORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN5 7XB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BROOKFIELD STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1LD | NZE (DFES Best View Scenario) | 2.5329 | 2.5289 | 2.5239 | 2.5189 | 2.5139 | 2.5069 | 2.5019 | 2.4959 | 2.4899 | 2.4849 | 2.4619 | 2.4449 | 2.4349 | 2.4269 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BTP | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN31 2RL | NZE (DFES Best View Scenario) | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3837 | 16.3827 | 16.3827 | 16.3827 | 16.3827 | 16.3817 | 16.3817 | 16.3807 | 16.3807 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BURLEY STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS3 1JY | NZE (DFES Best View Scenario) | 39.9601 | 39.9141 | 39.8631 | 39.8081 | 39.7471 | 39.6811 | 39.6171 | 39.5561 | 39.4941 | 39.4341 | 39.1871 | 39.0071 | 38.9001 | 38.8061 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BURMANTOFTS | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 7SS | NZE (DFES Best View Scenario) | 10.2865 | 10.2505 | 10.2105 | 10.1665 | 10.1185 | 10.0665 | 10.0155 | 9.9665 | 9.9185 | 9.8705 | 9.6755 | 9.5325 | 9.4475 | 9.3735 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BURNLEYVILLE | 11 | 33 | Heckmondwike | SKELTON GRANGE | BD19 4RY | NZE (DFES Best View Scenario) | 1.7804 | 1.6584 | 1.5224 | 1.3754 | 1.2114 | 1.0364 | 0.8674 | 0.7014 | 0.5364 | 0.3734 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BURTON PIDSEA | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU12 9AE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BURTON ROAD | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 2QG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 2HG | NZE (DFES Best View Scenario) | 10.7243 | 10.6113 | 10.4853 | 10.3503 | 10.1983 | 10.0373 | 9.8803 | 9.7273 | 9.5753 | 9.4263 | 8.8183 | 8.3743 | 8.1093 | 7.8783 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | BUTTERWICK | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO17 8HF | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CAISTOR | 11 | 33 | Wold Newton | KEADBY | LN7 6RE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CALDER WHARF | 11 | 33 | Thornhill 132kV | ELLAND | WF13 3JQ | NZE (DFES Best View Scenario) | 19.8008 | 19.6688 | 19.5218 | 19.3628 | 19.1858 | 18.9958 | 18.8118 | 18.6328 | 18.4538 | 18.2768 | 17.5538 | 17.0228 | 16.6998 | 16.4168 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CARLTON HILL | 11 | 33 | Leeds North | SKELTON GRANGE | LS7 1JB | NZE (DFES Best View Scenario) | 22.1734 | 22.1234 | 22.0684 | 22.0084 | 21.9424 | 21.8714 | 21.8024 | 21.7344 | 21.6684 | 21.6024 | 21.3354 | 21.1404 | 21.0234 | 20.9224 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CARR LANE | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 4PS | NZE (DFES Best View Scenario) | 22.3617 | 22.2437 | 22.1117 | 21.9697 | 21.8107 | 21.6417 | 21.4767 | 21.3167 | 21.1577 | 21.0007 | 20.3597 | 19.8907 | 19.6087 | 19.3637 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CHELKER RESERVOIR | 11 | 33 | Silsden | BRADFORD WEST | LS29 0JS | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CHEVIN END | 11 | 33 | Menston | BRADFORD WEST | LS29 6BE | NZE (DFES Best View Scenario) | 23.3545 | 23.2785 | 23.1935 | 23.1015 | 23.0005 | 22.8915 | 22.7855 | 22.6825 | 22.5805 | 22.4795 | 22.0685 | 21.7685 | 21.5895 | 21.4335 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CLARENCE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1JE | NZE (DFES Best View Scenario) | 7.613 | 7.585 | 7.554 | 7.52 | 7.483 | 7.443 | 7.404 | 7.366 | 7.328 | 7.291 | 7.141 | 7.031 | 6.965 | 6.908 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON ROAD | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS2 9JT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CLARENDON STREET | 11 | 33 | Hull South | CREYKE BECK | HU3 1AP | NZE (DFES Best View Scenario) | 22.2309 | 22.1689 | 22.0989 | 22.0239 | 21.9409 | 21.8509 | 21.7649 | 21.6809 | 21.5989 | 21.5179 | 21.1939 | 20.9609 | 20.8279 | 20.7159 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CLAYWHEELS LANE | 11 | 33 | Neepsend | NEEPSEND | S6 1LY | NZE (DFES Best View Scenario) | 22.4841 | 22.2861 | 22.0651 | 21.8271 | 21.5621 | 21.2791 | 21.0031 | 20.7361 | 20.4701 | 20.2081 | 19.1411 | 18.3621 | 17.8971 | 17.4921 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CLOUGH LANE | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3EH | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | COMMONSIDE LANE | 11 | 33 | Featherstone | FERRYBRIDGE B | WF7 5DF | NZE (DFES Best View Scenario) | 5.2718 | 5.1658 | 5.0478 | 5.6198 | 5.4778 | 5.3268 | 5.1788 | 5.0358 | 4.8938 | 4.7528 | 4.1788 | 3.7588 | 3.5068 | 3.2878 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CONVAMORE ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN32 9PG | NZE (DFES Best View Scenario) | 13.9683 | 13.8523 | 13.7223 | 13.5833 | 13.4283 | 13.2623 | 13.1003 | 12.9433 | 12.7873 | 12.6323 | 12.0013 | 11.5393 | 11.2603 | 11.0163 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CONYARD ROAD | 11 | 33 | Humberston | GRIMSBY WEST | DN35 7LQ | NZE (DFES Best View Scenario) | 10.6086 | 10.4536 | 10.2816 | 10.0956 | 9.8886 | 9.6676 | 9.4526 | 9.2436 | 9.0356 | 8.8296 | 7.9896 | 7.3736 | 7.0016 | 6.6756 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CORNWALL STREET | 11 | 132 | Cornwall Street | CREYKE BECK | HU8 8AQ | NZE (DFES Best View Scenario) | 32.3897 | 32.3297 | 32.2627 | 32.1907 | 32.1097 | 32.0227 | 31.9397 | 31.8587 | 31.7797 | 31.7007 | 31.3877 | 31.1627 | 31.0347 | 30.9257 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CORRINGHAM ROAD | 11 | 33 | Blyton | KEADBY | DN21 1FT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | COSTHORPE | 11 | 66 | Thurcroft | THURCROFT | S81 9QR | NZE (DFES Best View Scenario) | 6.5931 | 6.5121 | 6.4221 | 6.3241 | 6.2161 | 6.1001 | 5.9871 | 5.8751 | 5.7611 | 5.6481 | 5.1721 | 4.8111 | 4.5731 | 4.3581 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | COUNTY ROAD NORTH | 11 | 33 | Hull South | CREYKE BECK | HU5 5DR | NZE (DFES Best View Scenario) | 8.0954 | 7.8514 | 7.5774 | 7.2834 | 6.9564 | 6.6064 | 6.2654 | 5.9304 | 5.5954 | 5.2614 | 3.8794 | 2.8464 | 2.1954 | 1.6134 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CRACOE | 11 | 33 | Silsden | BRADFORD WEST | BD23 6BE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CROOKESMOOR ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 3FP | NZE (DFES Best View Scenario) | 3.4497 | 3.2907 | 3.1137 | 2.9227 | 2.7097 | 2.4827 | 2.2617 | 2.0477 | 1.8347 | 1.6237 | 0.76771 | 0.14371 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CROSSHILLS | 11 | 33 | Silsden | BRADFORD WEST | BD20 7AQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CROWLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN17 4BB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | CROWN STREET | 11 | 33 | Girlington | BRADFORD WEST | BD1 2LA | NZE (DFES Best View Scenario) | 0.76871 | 0.75171 | 0.73171 | 0.71171 | 0.68771 | 0.66371 | 0.63871 | 0.61571 | 0.59271 | 0.56971 | 0.47571 | 0.40771 | 0.36671 | 0.33071 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DALTON | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD2 1FF | NZE (DFES Best View Scenario) | 2.566 | 2.389 | 2.192 | 1.979 | 1.743 | 1.49 | 1.244 | 1.004 | 0.765 | 0.529 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DARNALL | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 4JT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DEARNE ROAD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DEIGHTON | 11 | 33 | Brighouse 132/33kV | ELLAND | HD2 1UP | NZE (DFES Best View Scenario) | 18.37 | 18.269 | 18.156 | 18.035 | 17.9 | 17.755 | 17.614 | 17.477 | 17.34 | 17.205 | 16.652 | 16.245 | 15.998 | 15.781 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DENBY DALE ROAD | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF2 7BH | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DENBY GRANGE | 11 | 33 | Thornhill 132kV | ELLAND | WF4 4JG | NZE (DFES Best View Scenario) | 0.29111 | 0.25411 | 0.21211 | 0.16711 | 0.11711 | 0.06311 | 0.01111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DENHOLME | 11 | 33 | Holmfield | BRADFORD WEST | BD13 4JF | NZE (DFES Best View Scenario) | 11.5747 | 11.5387 | 11.4987 | 11.4557 | 11.4067 | 11.3557 | 11.3057 | 11.2567 | 11.2087 | 11.1607 | 10.9667 | 10.8257 | 10.7407 | 10.6667 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DINNINGTON | 11 | 66 | Thurcroft | THURCROFT | S25 3QT | NZE (DFES Best View Scenario) | 0 | 22.1947 | 22.0217 | 21.8347 | 21.6277 | 21.4057 | 21.1897 | 20.9797 | 20.7707 | 20.5637 | 19.7177 | 19.0977 | 18.7217 | 18.3927 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DOUGHTY ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN32 0LR | NZE (DFES Best View Scenario) | 3.7128 | 3.4958 | 3.2518 | 2.9898 | 2.6978 | 2.3858 | 2.0828 | 1.7868 | 1.4928 | 1.2028 | 0.016799 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DOWKER STREET | 11 | 33 | Lindley | ELLAND | HD3 4JB | NZE (DFES Best View Scenario) | 0.44451 | 0.35151 | 0.24751 | 0.13651 | 0.012515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DRAX PRIMARY | 11 | 66 | Camblesforth | CAMBLESFORTH | YO8 6PQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DRIFFIELD | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 5XR | NZE (DFES Best View Scenario) | 13.6115 | 13.2715 | 12.8915 | 12.4825 | 12.0335 | 11.5495 | 11.0705 | 10.5905 | 10.0975 | 9.5965 | 7.4325 | 5.7255 | 4.5225 | 3.3985 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DRONFIELD | 11 | 33 | Jordanthorpe | JORDANTHORPE | S18 2XU | NZE (DFES Best View Scenario) | 1.6382 | 1.5652 | 1.4832 | 1.3942 | 1.2972 | 1.1922 | 1.0892 | 0.9882 | 0.8862 | 0.7852 | 0.3622 | 0.042205 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DUDLEY HILL | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9NW | NZE (DFES Best View Scenario) | 23.1088 | 23.0378 | 22.9588 | 22.8728 | 22.7768 | 22.6748 | 22.5758 | 22.4788 | 22.3828 | 22.2888 | 21.9028 | 21.6218 | 21.4528 | 21.3058 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DUNKESWICK | 11 | 33 | Bramham | FERRYBRIDGE B | LS17 9LP | NZE (DFES Best View Scenario) | 11.9103 | 11.7573 | 11.5853 | 11.4003 | 11.1953 | 10.9753 | 10.7613 | 10.5503 | 10.3393 | 10.1303 | 9.2613 | 8.6123 | 8.2023 | 7.8363 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | DURKAR LOW LANE | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF4 3BJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | EASINGTON | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0SU | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | EASTFIELD ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ECCLESFIELD | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 9YR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | EDLINGTON | 11 | 66 | Thurcroft | THURCROFT | DN12 1SU | NZE (DFES Best View Scenario) | 13.4505 | 13.2675 | 13.0625 | 12.8425 | 12.5975 | 12.3355 | 12.0795 | 11.8285 | 11.5775 | 11.3275 | 10.2935 | 9.5215 | 9.0345 | 8.6005 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | EGGBOROUGH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | DN14 0QA | NZE (DFES Best View Scenario) | 7.4016 | 7.3626 | 7.3186 | 7.2706 | 7.2186 | 7.1626 | 7.1066 | 7.0516 | 6.9946 | 6.9366 | 6.6866 | 6.4896 | 6.3516 | 6.2226 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ELGAR ROAD | 11 | 33 | Hull West | CREYKE BECK | HU4 7NY | NZE (DFES Best View Scenario) | 21.7787 | 21.5087 | 21.2077 | 20.8847 | 20.5277 | 20.1427 | 19.7647 | 19.3887 | 19.0067 | 18.6207 | 16.9777 | 15.7047 | 14.8387 | 14.0407 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ELLAND 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX5 9AE | NZE (DFES Best View Scenario) | 19.9315 | 19.8465 | 19.7505 | 19.6485 | 19.5345 | 19.4125 | 19.2935 | 19.1765 | 19.0585 | 18.9405 | 18.4495 | 18.0795 | 17.8405 | 17.6255 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ELLIFOOT LANE | 11 | 33 | Saltend 132/33kV | SALTEND NORTH | HU12 9EB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 1/3 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | NZE (DFES Best View Scenario) | 4.7608 | 4.6978 | 4.6268 | 4.5508 | 4.4658 | 4.3748 | 4.2868 | 4.2018 | 4.1168 | 4.0328 | 3.6918 | 3.4418 | 3.2938 | 3.1638 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ELLIN STREET 2 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4QZ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 1 | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ELMHIRST LANE 2 | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S75 4LS | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ELSECAR | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S74 8AU | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ENDIKE LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 8AY | NZE (DFES Best View Scenario) | 16.4144 | 16.2604 | 16.0884 | 15.9024 | 15.6964 | 15.4764 | 15.2604 | 15.0484 | 14.8354 | 14.6234 | 13.7374 | 13.0704 | 12.6424 | 12.2584 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | EPWORTH | 11 | 33 | Blyton | KEADBY | DN9 1JU | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FARNLEY CRESCENT | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 5AN | NZE (DFES Best View Scenario) | 0.75508 | 0.62908 | 0.48708 | 0.33508 | 0.16508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FENTON LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6EZ | NZE (DFES Best View Scenario) | 5.0532 | 4.9932 | 4.9262 | 4.8542 | 4.7752 | 4.6902 | 4.6062 | 4.5222 | 4.4352 | 4.3472 | 3.9692 | 3.6702 | 3.4612 | 3.2662 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF11 8RR | NZE (DFES Best View Scenario) | 1.967 | 1.694 | 1.388 | 1.06 | 0.695 | 0.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FIR TREE LANE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS17 7BZ | NZE (DFES Best View Scenario) | 3.7558 | 3.5968 | 3.4188 | 3.2268 | 3.0128 | 2.7838 | 2.5618 | 2.3458 | 2.1308 | 1.9198 | 1.0588 | 0.43076 | 0.05576 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FIRST AVENUE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU6 9NE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FIRTH BROWN | 11 | 33 | Santon | KEADBY | DN16 1XP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FISH DAM LANE | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 3HQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FLIXBOROUGH | 11 | 33 | Scunthorpe North | KEADBY | DN15 8RR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FOLLY HALL | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 3TF | NZE (DFES Best View Scenario) | 1.7547 | 1.6797 | 1.5957 | 1.5047 | 1.4037 | 1.2957 | 1.1907 | 1.0887 | 0.9867 | 0.8857 | 0.4737 | 0.1707 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FOUR LANE ENDS | 11 | 33 | Girlington | BRADFORD WEST | BD8 0LJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FOXHILLS | 11 | 33 | Scunthorpe North | KEADBY | DN15 8QW | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FULLERTON ROAD | 11 | 33 | Templeborough 275/33KV | TEMPLEBOROUGH 275/33KV | S60 1DL | NZE (DFES Best View Scenario) | 0.06487 | 0.0028698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | FURNESS AVENUE | 11 | 33 | Holmfield | BRADFORD WEST | WF8 3JA | NZE (DFES Best View Scenario) | 1.0469 | 0.91386 | 0.76586 | 0.60686 | 0.43086 | 0.24186 | 0.056864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GAISBY LANE | 11 | 33 | Bradford | BRADFORD WEST | BD2 1BB | NZE (DFES Best View Scenario) | 3.041 | 2.912 | 2.769 | 2.615 | 2.443 | 2.26 | 2.081 | 1.907 | 1.735 | 1.565 | 0.87198 | 0.36598 | 0.062984 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GIBRALTAR ROAD | 11 | 33 | Holmfield | BRADFORD WEST | HX1 4HL | NZE (DFES Best View Scenario) | 4.2051 | 4.0221 | 3.8181 | 3.5991 | 3.3561 | 3.0951 | 2.8401 | 2.5881 | 2.3361 | 2.0831 | 1.0271 | 0.2281 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GIBSON LANE | 11 | 33 | Hull West | CREYKE BECK | HU14 3HH | NZE (DFES Best View Scenario) | 16.888 | 16.631 | 16.345 | 16.037 | 15.699 | 15.334 | 14.973 | 14.611 | 14.24 | 13.863 | 12.233 | 10.946 | 10.04 | 9.193 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GILDERSOME | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 7HW | NZE (DFES Best View Scenario) | 0.60687 | 0.53487 | 0.45387 | 0.36687 | 0.26987 | 0.16687 | 0.066867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GLEADLESS VALLEY | 11 | 33 | Norton Lees | NORTON LEES | S14 1FP | NZE (DFES Best View Scenario) | 1.682 | 1.551 | 1.404 | 1.246 | 1.069 | 0.88098 | 0.69798 | 0.51998 | 0.34298 | 0.16898 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GOOLE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 6SX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GRAINTHORPE | 11 | 33 | Wold Newton | KEADBY | LN11 7JU | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GREAT COATES | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN37 9PN | NZE (DFES Best View Scenario) | 2.0421 | 1.8671 | 1.6711 | 1.4611 | 1.2261 | 0.97609 | 0.73209 | 0.49409 | 0.25809 | 0.025087 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GREENHILL | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 7RJ | NZE (DFES Best View Scenario) | 0.81423 | 0.73623 | 0.64723 | 0.55323 | 0.44723 | 0.33423 | 0.22423 | 0.11723 | 0.010233 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS RD | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | Doncaster Central | WEST MELTON / THORPE MARSH | DN1 1QN | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GRIMETHORPE | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S72 7BQ | NZE (DFES Best View Scenario) | 15.4899 | 15.4099 | 15.3209 | 15.2239 | 15.1169 | 15.0029 | 14.8909 | 14.7819 | 14.6729 | 14.5649 | 14.1199 | 13.7909 | 13.5869 | 13.4069 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GROVE STREET | 11 | 33 | Lindley | ELLAND | HD1 2PB | NZE (DFES Best View Scenario) | 13.6602 | 13.6342 | 13.6062 | 13.5752 | 13.5412 | 13.5042 | 13.4682 | 13.4342 | 13.3992 | 13.3652 | 13.2252 | 13.1222 | 13.0592 | 13.0042 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | GUARDIAN GLASS | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8GA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HACKENTHORPE | 11 | 66 | Thurcroft | THURCROFT | S12 4ET | NZE (DFES Best View Scenario) | 24.1276 | 23.9946 | 23.8456 | 23.6856 | 23.5066 | 23.3156 | 23.1296 | 22.9496 | 22.7706 | 22.5936 | 21.8736 | 21.3486 | 21.0356 | 20.7626 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HALIFAX 33/11KV | 11 | 33 | Halifax 132/33kV | ELLAND | HX1 1XB | NZE (DFES Best View Scenario) | 2.3276 | 2.2076 | 2.0736 | 1.9296 | 1.7696 | 1.5986 | 1.4306 | 1.2656 | 1.0996 | 0.93262 | 0.23862 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HALLAM STREET | 11 | 33 | Menston | BRADFORD WEST | LS20 8AG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HARDEN | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD16 1BG | NZE (DFES Best View Scenario) | 6.1103 | 6.0713 | 6.0283 | 5.9823 | 5.9313 | 5.8763 | 5.8223 | 5.7703 | 5.7193 | 5.6683 | 5.4613 | 5.3093 | 5.2183 | 5.1393 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HARPSWELL | 11 | 33 | Blyton | KEADBY | DN21 5UT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HARWORTH | 11 | 66 | Thurcroft | THURCROFT | DN11 8JW | NZE (DFES Best View Scenario) | 19.5045 | 19.4155 | 19.3165 | 19.2095 | 19.0915 | 18.9645 | 18.8405 | 18.7185 | 18.5955 | 18.4735 | 17.9605 | 17.5735 | 17.3235 | 17.0975 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 1 | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD22 9EP | NZE (DFES Best View Scenario) | 13.6306 | 13.5716 | 13.5066 | 13.4356 | 13.3576 | 13.2736 | 13.1916 | 13.1126 | 13.0336 | 12.9556 | 12.6386 | 12.4076 | 12.2686 | 12.1486 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HAWORTH 2 | 11 | 33 | Silsden | BRADFORD WEST | BD22 9EP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HAXEY | 11 | 33 | Blyton | KEADBY | DN9 2LT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HAYTON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO42 1RJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 15.7365 | 15.4905 | 15.2255 | 14.9625 | 14.6995 | 14.4305 | 14.1555 | 12.9705 | 12.0355 | 11.3775 | 10.7615 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HAZLEHEAD | 11 | 33 | Thornhill 132kV | ELLAND | S36 4HG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HEBDEN BRIDGE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 6LX | NZE (DFES Best View Scenario) | 7.4667 | 7.4297 | 7.3887 | 7.3447 | 7.2957 | 7.2437 | 7.1917 | 7.1417 | 7.0907 | 7.0397 | 6.8277 | 6.6667 | 6.5627 | 6.4697 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HEDLEY CHASE | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS12 1YN | NZE (DFES Best View Scenario) | 12.6728 | 12.6418 | 12.6078 | 12.5718 | 12.5308 | 12.4868 | 12.4448 | 12.4028 | 12.3618 | 12.3218 | 12.1578 | 12.0378 | 11.9658 | 11.9038 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HEDON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 8ED | NZE (DFES Best View Scenario) | 11.4045 | 11.3945 | 11.3845 | 11.3735 | 11.3605 | 11.3475 | 11.3345 | 11.3225 | 11.3105 | 11.2985 | 11.2505 | 11.2155 | 11.1955 | 11.1795 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HEMSWORTH | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 5BZ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 1 | 11 | 33 | Hull South | CREYKE BECK | HU4 6SP | NZE (DFES Best View Scenario) | 0.81984 | 0.75584 | 0.68384 | 0.60684 | 0.52184 | 0.42984 | 0.33984 | 0.25084 | 0.15984 | 0.067839 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HESSLE ROAD 2 | 11 | 33 | Hull West | CREYKE BECK | HU4 6SP | NZE (DFES Best View Scenario) | 1.4475 | 1.3875 | 1.3195 | 1.2475 | 1.1675 | 1.0815 | 0.99652 | 0.91252 | 0.82752 | 0.74252 | 0.38052 | 0.10252 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HIBALDSTOW | 11 | 33 | Santon | KEADBY | DN21 4NH | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HICKLETON | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | S63 0DE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HILLCREST | 11 | 33 | Leeds East | SKELTON GRANGE | LS8 3AA | NZE (DFES Best View Scenario) | 3.3989 | 3.2459 | 3.0759 | 2.8919 | 2.6869 | 2.4679 | 2.2559 | 2.0489 | 1.8439 | 1.6419 | 0.81793 | 0.21693 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HOLBECK | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9SZ | NZE (DFES Best View Scenario) | 3.97 | 3.853 | 3.723 | 3.582 | 3.425 | 3.258 | 3.095 | 2.937 | 2.78 | 2.625 | 1.995 | 1.535 | 1.261 | 1.022 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HOLDERNESS | 11 | 33 | Bransholme | CREYKE BECK | HU9 4AU | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 4BX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 20.2495 | 20.1415 | 20.0325 | 19.9215 | 19.8085 | 19.3215 | 18.9375 | 18.6675 | 18.4155 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HONLEY | 11 | 33 | Lindley | ELLAND | HD9 6RU | NZE (DFES Best View Scenario) | 10.3309 | 10.2079 | 10.0699 | 9.9219 | 9.7569 | 9.5799 | 9.4089 | 9.2409 | 9.0739 | 8.9099 | 8.2349 | 7.7389 | 7.4379 | 7.1729 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HOPE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S33 6RP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HORBURY | 11 | 33 | Thornhill 132kV | ELLAND | WF4 6EU | NZE (DFES Best View Scenario) | 17.8573 | 17.7143 | 17.5553 | 17.3833 | 17.1923 | 16.9873 | 16.7883 | 16.5953 | 16.4023 | 16.2133 | 15.4383 | 14.8723 | 14.5323 | 14.2353 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HOUGHTON MAIN | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S72 0GX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HULL EAST 33/11KV | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5NP | NZE (DFES Best View Scenario) | 22.5806 | 22.3766 | 22.1496 | 21.9046 | 21.6356 | 21.3466 | 21.0606 | 20.7746 | 20.4826 | 20.1866 | 18.9166 | 17.9216 | 17.2316 | 16.5906 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HUMBER ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 3LZ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | HUNMANBY | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO14 0JY | NZE (DFES Best View Scenario) | 20.0455 | 19.8255 | 19.5795 | 19.3165 | 19.0245 | 18.7115 | 18.4035 | 18.0985 | 17.7895 | 17.4795 | 16.1675 | 15.1615 | 14.4905 | 13.8765 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ICI FIBRES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4LT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | IDLE | 11 | 33 | Bradford | BRADFORD WEST | BD10 8SA | NZE (DFES Best View Scenario) | 2.5481 | 2.4101 | 2.2541 | 2.0871 | 1.9011 | 1.7021 | 1.5091 | 1.3211 | 1.1341 | 0.95005 | 0.19905 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ILKLEY | 11 | 33 | Silsden | BRADFORD WEST | LS29 9BE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | INGS LANE | 11 | 33 | Silsden | BRADFORD WEST | BD23 1UP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | IVESON HOUSE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 6RF | NZE (DFES Best View Scenario) | 20.7756 | 20.6326 | 20.4716 | 20.2986 | 20.1056 | 19.8986 | 19.6986 | 19.5036 | 19.3106 | 19.1196 | 18.3426 | 17.7766 | 17.4386 | 17.1446 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | JARRATT STREET | 11 | 33 | Mallard Way | WEST MELTON / THORPE MARSH | DN1 2BS | NZE (DFES Best View Scenario) | 13.0298 | 12.9318 | 12.8218 | 12.7038 | 12.5728 | 12.4318 | 12.2948 | 12.1608 | 12.0258 | 11.8928 | 11.3388 | 10.9248 | 10.6638 | 10.4318 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KEDDINGTON ROAD | 11 | 33 | Wold Newton | KEADBY | LN11 0DE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KEIGHLEY | 11 | 132 | Keighley | BRADFORD WEST | BD21 5AJ | NZE (DFES Best View Scenario) | 30.3639 | 30.2859 | 30.1989 | 30.1049 | 29.9999 | 29.8889 | 29.7799 | 29.6739 | 29.5689 | 29.4659 | 29.0439 | 28.7359 | 28.5509 | 28.3909 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KENMORE ROAD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF2 0XE | NZE (DFES Best View Scenario) | 18.8329 | 18.7679 | 18.6959 | 18.6169 | 18.5299 | 18.4369 | 18.3459 | 18.2579 | 18.1699 | 18.0839 | 17.7309 | 17.4729 | 17.3179 | 17.1829 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KILLINGHALL ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD3 8HN | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KILNHURST | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S64 5TL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KING GEORGE DOCK | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU9 5PL | NZE (DFES Best View Scenario) | 23.854 | 23.847 | 23.839 | 23.83 | 23.821 | 23.811 | 23.801 | 23.792 | 23.782 | 23.773 | 23.736 | 23.71 | 23.695 | 23.682 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KIRK DRIVE | 11 | 33 | Menston | BRADFORD WEST | BD17 6SA | NZE (DFES Best View Scenario) | 0.98938 | 0.89338 | 0.78738 | 0.67238 | 0.54538 | 0.40838 | 0.27538 | 0.14638 | 0.018381 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KIRK SANDALL | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 1QP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KIRKBURN | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO25 9EH | NZE (DFES Best View Scenario) | 6.0892 | 6.0072 | 5.9162 | 5.8182 | 5.7102 | 5.5942 | 5.4792 | 5.3642 | 5.2472 | 5.1282 | 4.6192 | 4.2212 | 3.9442 | 3.6872 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KIVETON PARK | 11 | 66 | Thurcroft | THURCROFT | S26 6RP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | KNOSTROP | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0PJ | NZE (DFES Best View Scenario) | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | 17.2733 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LEA ROAD | 11 | 33 | Blyton | KEADBY | DN21 1ND | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LEASOWE ROAD | 11 | 33 | Low Road | SKELTON GRANGE | LS10 2EY | NZE (DFES Best View Scenario) | 6.788 | 6.711 | 6.625 | 6.532 | 6.429 | 6.319 | 6.212 | 6.108 | 6.004 | 5.903 | 5.488 | 5.185 | 5.004 | 4.847 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LEDSTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF10 2AX | NZE (DFES Best View Scenario) | 1.2288 | 1.1138 | 0.9858 | 0.8478 | 0.6948 | 0.5298 | 0.3708 | 0.2148 | 0.060795 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LEEDS ROAD | 11 | 33 | Bramham | FERRYBRIDGE B | LS22 5AA | NZE (DFES Best View Scenario) | 0.35349 | 0.30449 | 0.24949 | 0.19049 | 0.12449 | 0.054491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LEGRAMS MILL LANE | 11 | 33 | Girlington | BRADFORD WEST | BD7 2BA | NZE (DFES Best View Scenario) | 21.1828 | 21.1028 | 21.0138 | 20.9178 | 20.8108 | 20.6958 | 20.5848 | 20.4768 | 20.3688 | 20.2628 | 19.8308 | 19.5158 | 19.3268 | 19.1618 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LEYLANDS ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS2 7QB | NZE (DFES Best View Scenario) | 16.1332 | 16.1112 | 16.0862 | 16.0592 | 16.0282 | 15.9962 | 15.9652 | 15.9342 | 15.9042 | 15.8742 | 15.7532 | 15.6642 | 15.6112 | 15.5652 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LIVERSEDGE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF15 7NY | NZE (DFES Best View Scenario) | 1.7149 | 1.6289 | 1.5319 | 1.4289 | 1.3129 | 1.1899 | 1.0689 | 0.95188 | 0.83588 | 0.72088 | 0.24888 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LOUTH | 11 | 33 | Wold Newton | KEADBY | LN11 0WA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LOW MOOR | 11 | 33 | Staygate | SKELTON GRANGE | BD12 0NG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LOWFIELDS | 11 | 33 | Brighouse 132/33kV | ELLAND | HX5 9DE | NZE (DFES Best View Scenario) | 25.255 | 25.253 | 25.249 | 25.246 | 25.242 | 25.238 | 25.234 | 25.23 | 25.226 | 25.222 | 25.205 | 25.192 | 25.184 | 25.177 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | LOXLEY ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 6SJ | NZE (DFES Best View Scenario) | 0.24226 | 0.23526 | 0.22626 | 0.21726 | 0.20726 | 0.19626 | 0.18526 | 0.17526 | 0.16426 | 0.15426 | 0.11326 | 0.083257 | 0.065257 | 0.049257 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MANCHESTER ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD5 0QL | NZE (DFES Best View Scenario) | 3.0677 | 3.0437 | 3.0167 | 2.9877 | 2.9547 | 2.9207 | 2.8867 | 2.8547 | 2.8217 | 2.7897 | 2.6597 | 2.5647 | 2.5077 | 2.4577 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 1 | 11 | 33 | Sheffield City | SHEFFIELD CITY | S12 2DL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MANSFIELD ROAD 2 | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S12 2DL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MARKHAM GATES | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 2FS | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MARMION ROAD | 11 | 33 | Norton Lees | NORTON LEES | S11 8TS | NZE (DFES Best View Scenario) | 2.5128 | 2.3408 | 2.1478 | 1.9408 | 1.7098 | 1.4628 | 1.2228 | 0.9888 | 0.7578 | 0.5288 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MARSDEN ROAD | 11 | 33 | Moss Road | GRIMSBY WEST | DN31 3SQ | NZE (DFES Best View Scenario) | 4.9539 | 4.8689 | 4.7739 | 4.6719 | 4.5579 | 4.4359 | 4.3169 | 4.2019 | 4.0869 | 3.9739 | 3.5099 | 3.1699 | 2.9649 | 2.7859 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MARTONGATE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO16 6RX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 18.3215 | 17.8915 | 17.4265 | 16.9675 | 16.5065 | 16.0335 | 15.5535 | 13.4775 | 11.8395 | 10.6855 | 9.6075 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MELTHAM | 11 | 33 | Lindley | ELLAND | HD9 4AL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MEXBOROUGH 1_2 | 11 | 66 | Thurcroft | THURCROFT | S64 0JD | NZE (DFES Best View Scenario) | 24.453 | 24.197 | 23.91 | 23.602 | 23.259 | 22.892 | 22.534 | 22.183 | 21.832 | 21.483 | 20.037 | 18.959 | 18.28 | 17.675 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MIDDLETON TOWN STREET | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS10 3TQ | NZE (DFES Best View Scenario) | 16.3 | 16.173 | 16.031 | 15.878 | 15.708 | 15.526 | 15.35 | 15.178 | 15.007 | 14.839 | 14.155 | 13.655 | 13.357 | 13.098 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MILLHOUSES | 11 | 33 | Jordanthorpe | JORDANTHORPE | S7 2QH | NZE (DFES Best View Scenario) | 1.2305 | 1.1675 | 1.0975 | 1.0215 | 0.93752 | 0.84752 | 0.75952 | 0.67452 | 0.59052 | 0.50652 | 0.16752 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MILLROYD STREET | 11 | 33 | Brighouse 132/33kV | ELLAND | HD6 1JZ | NZE (DFES Best View Scenario) | 14.2317 | 14.1107 | 13.9757 | 13.8307 | 13.6697 | 13.4967 | 13.3277 | 13.1607 | 12.9937 | 12.8267 | 12.1287 | 11.6017 | 11.2627 | 10.9567 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MILTON PLACE | 11 | 33 | Wakefield North | SKELTON GRANGE | WF5 9EG | NZE (DFES Best View Scenario) | 18.5497 | 18.3767 | 18.1827 | 17.9747 | 17.7417 | 17.4937 | 17.2517 | 17.0167 | 16.7827 | 16.5527 | 15.6107 | 14.9217 | 14.5067 | 14.1447 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MIRFIELD | 11 | 33 | Thornhill 132kV | ELLAND | WF14 8NF | NZE (DFES Best View Scenario) | 19.461 | 19.306 | 19.134 | 18.947 | 18.74 | 18.518 | 18.303 | 18.093 | 17.883 | 17.677 | 16.83 | 16.207 | 15.829 | 15.497 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MONCKTON | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | S71 4BG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MOOR ROAD | 11 | 33 | Leeds North | SKELTON GRANGE | LS6 4BJ | NZE (DFES Best View Scenario) | 23.1316 | 22.9666 | 22.7816 | 22.5836 | 22.3616 | 22.1246 | 21.8956 | 21.6716 | 21.4496 | 21.2316 | 20.3406 | 19.6906 | 19.3026 | 18.9656 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MOORSIDE ROAD | 11 | 33 | Bradford | BRADFORD WEST | BD2 3RJ | NZE (DFES Best View Scenario) | 20.1099 | 19.9639 | 19.8009 | 19.6259 | 19.4309 | 19.2219 | 19.0189 | 18.8209 | 18.6259 | 18.4319 | 17.6439 | 17.0679 | 16.7239 | 16.4239 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MORLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS27 9HS | NZE (DFES Best View Scenario) | 19.7657 | 19.6407 | 19.5017 | 19.3517 | 19.1847 | 19.0057 | 18.8327 | 18.6637 | 18.4957 | 18.3307 | 17.6577 | 17.1677 | 16.8747 | 16.6197 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MOUNT STREET | 11 | 33 | Bradford | BRADFORD WEST | BD4 8TB | NZE (DFES Best View Scenario) | 20.99 | 20.956 | 20.917 | 20.875 | 20.829 | 20.779 | 20.731 | 20.684 | 20.637 | 20.591 | 20.403 | 20.266 | 20.184 | 20.112 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | MYTHOLMROYD | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX7 8NE | NZE (DFES Best View Scenario) | 13.7341 | 13.6671 | 13.5931 | 13.5121 | 13.4231 | 13.3281 | 13.2341 | 13.1421 | 13.0491 | 12.9571 | 12.5701 | 12.2771 | 12.0881 | 11.9171 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NAB LANE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 9NE | NZE (DFES Best View Scenario) | 11.9506 | 11.8726 | 11.7866 | 11.6936 | 11.5896 | 11.4786 | 11.3706 | 11.2656 | 11.1606 | 11.0576 | 10.6336 | 10.3226 | 10.1336 | 9.9676 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NABWOOD | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD18 4AA | NZE (DFES Best View Scenario) | 13.3561 | 13.2441 | 13.1181 | 12.9831 | 12.8321 | 12.6711 | 12.5141 | 12.3621 | 12.2111 | 12.0621 | 11.4531 | 11.0091 | 10.7431 | 10.5121 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NATIONAL AVENUE | 11 | 33 | Hull South | CREYKE BECK | HU5 4JN | NZE (DFES Best View Scenario) | 0.74237 | 0.67537 | 0.60137 | 0.52137 | 0.43137 | 0.33637 | 0.24437 | 0.15437 | 0.066373 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | Wincobank | WINCOBANK | S61 2DL | NZE (DFES Best View Scenario) | 18.8702 | 18.7492 | 18.6142 | 18.4682 | 18.3062 | 18.1332 | 17.9652 | 17.8002 | 17.6372 | 17.4762 | 16.8162 | 16.3322 | 16.0382 | 15.7812 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NEW ORCHARD LANE | 11 | 66 | Thurcroft | THURCROFT | S66 9HY | NZE (DFES Best View Scenario) | 1.1492 | 1.0452 | 0.92715 | 0.80115 | 0.66115 | 0.51115 | 0.36515 | 0.22315 | 0.081153 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NEWHALL ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 2RS | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2933 | 1.2483 | 1.2043 | 1.0233 | 0.8923 | 0.8133 | 0.7453 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 1 | 11 | 33 | Hull West | CREYKE BECK | HU15 2QU | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NEWPORT 2 | 11 | 33 | Osgodby 3/4 | DRAX | HU15 2QU | NZE (DFES Best View Scenario) | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | 8.5787 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NINELANDS LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS25 2PE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NORFOLK PARK | 11 | 33 | Norton Lees | NORTON LEES | S2 3UU | NZE (DFES Best View Scenario) | 0.52939 | 0.40039 | 0.25639 | 0.10239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NORMANBY | 11 | 33 | Blyton | KEADBY | LN8 2HQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NORMANTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF6 2JA | NZE (DFES Best View Scenario) | 4.5197 | 4.3847 | 4.2337 | 4.0717 | 3.8907 | 3.6967 | 3.5087 | 3.3257 | 3.1437 | 2.9637 | 2.2317 | 1.6957 | 1.3737 | 1.0927 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NORTH AVENUE | 11 | 33 | Menston | BRADFORD WEST | LS21 1SX | NZE (DFES Best View Scenario) | 19.1456 | 19.0336 | 18.9096 | 18.7756 | 18.6266 | 18.4666 | 18.3116 | 18.1606 | 18.0116 | 17.8636 | 17.2626 | 16.8236 | 16.5616 | 16.3336 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NORTH THORESBY | 11 | 33 | Wold Newton | KEADBY | DN36 5SB | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | NORWOOD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 9JR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | OAKES ROAD | 11 | 33 | Lindley | ELLAND | HD3 3EW | NZE (DFES Best View Scenario) | 2.4498 | 2.3148 | 2.1638 | 2.0018 | 1.8208 | 1.6268 | 1.4388 | 1.2558 | 1.0738 | 0.89282 | 0.15382 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | OAKWOOD LANE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 3LF | NZE (DFES Best View Scenario) | 19.5121 | 19.4121 | 19.3001 | 19.1801 | 19.0461 | 18.9031 | 18.7641 | 18.6291 | 18.4941 | 18.3621 | 17.8231 | 17.4301 | 17.1961 | 16.9921 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ODSAL | 11 | 33 | Staygate | SKELTON GRANGE | BD6 1BW | NZE (DFES Best View Scenario) | 2.6126 | 2.4896 | 2.3526 | 2.2056 | 2.0406 | 1.8646 | 1.6946 | 1.5286 | 1.3636 | 1.2006 | 0.5376 | 0.053604 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | OLYMPIA MILLS | 11 | 33 | Osgodby 3/4 | DRAX | YO8 7AG | NZE (DFES Best View Scenario) | 19.6371 | 19.4131 | 19.1631 | 18.8941 | 18.5981 | 18.2801 | 17.9641 | 17.6491 | 17.3251 | 16.9971 | 15.5791 | 14.4631 | 13.6801 | 12.9491 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ORGREAVE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 9NA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | OUTWOOD | 11 | 33 | Wakefield North | SKELTON GRANGE | WF3 3TA | NZE (DFES Best View Scenario) | 1.7357 | 1.5987 | 1.4447 | 1.2797 | 1.0957 | 0.89866 | 0.70766 | 0.52166 | 0.33666 | 0.15466 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | PARK HILL | 11 | 33 | Sheffield City | SHEFFIELD CITY | S2 5QY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2402 | 1.1702 | 1.1022 | 0.82223 | 0.61723 | 0.49523 | 0.38923 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | PARK ROAD | 11 | 33 | Thornhill 132kV | ELLAND | WF12 9LW | NZE (DFES Best View Scenario) | 1.1138 | 1.0038 | 0.87983 | 0.74683 | 0.59783 | 0.43883 | 0.28483 | 0.13383 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | PARK STREET | 11 | 132 | Park Street | WEST MELTON / THORPE MARSH | S61 1TF | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | PASTURE ROAD SOUTH | 11 | 33 | Santon | KEADBY | DN18 5RX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | PATRINGTON ROAD | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU12 0AD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 6BG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | PENISTONE ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 2FL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | PLANGEO | 11 | 33 | Hull South | CREYKE BECK | HU3 6EG | NZE (DFES Best View Scenario) | 3.4984 | 3.3624 | 3.2104 | 3.0474 | 2.8644 | 2.6694 | 2.4814 | 2.2984 | 2.1194 | 1.9424 | 1.2344 | 0.72637 | 0.43737 | 0.19137 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | POLLINGTON | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | DN14 0RR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 0JG | NZE (DFES Best View Scenario) | 1.7218 | 1.6888 | 1.6518 | 1.6118 | 1.5668 | 1.5198 | 1.4738 | 1.4288 | 1.3848 | 1.3408 | 1.1618 | 1.0318 | 0.95476 | 0.88676 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | POOL | 11 | 33 | Menston | BRADFORD WEST | LS21 1RP | NZE (DFES Best View Scenario) | 16.3725 | 16.3425 | 16.3095 | 16.2735 | 16.2335 | 16.1905 | 16.1485 | 16.1075 | 16.0675 | 16.0275 | 15.8635 | 15.7425 | 15.6695 | 15.6045 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | PRINCE OF WALES | 11 | 33 | Featherstone | FERRYBRIDGE B | WF8 4PR | NZE (DFES Best View Scenario) | 10.7795 | 10.6255 | 10.4525 | 10.2665 | 10.0595 | 9.8375 | 9.6225 | 9.4125 | 9.2045 | 8.9995 | 8.1615 | 7.5485 | 7.1805 | 6.8585 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | PROSPECT ROAD | 11 | 33 | Lindley | ELLAND | HD3 4UY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | QUEENS ROAD | 11 | 33 | Immingham | GRIMSBY WEST | DN40 2LZ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | QUEENSBURY | 11 | 33 | Holmfield | BRADFORD WEST | HX3 7TJ | NZE (DFES Best View Scenario) | 25.4334 | 25.2694 | 25.0874 | 24.8904 | 24.6714 | 24.4374 | 24.2094 | 23.9854 | 23.7624 | 23.5404 | 22.6234 | 21.9424 | 21.5164 | 21.1384 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | RAWCLIFFE | 11 | 66 | Camblesforth | CAMBLESFORTH | DN14 8PQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | RAWDON | 11 | 33 | Rodley | SKELTON GRANGE | LS19 7BZ | NZE (DFES Best View Scenario) | 23.8076 | 23.6956 | 23.5706 | 23.4356 | 23.2846 | 23.1236 | 22.9676 | 22.8156 | 22.6646 | 22.5166 | 21.9106 | 21.4686 | 21.2046 | 20.9756 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | Rawmarsh Road 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | Rawmarsh Road 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON ROAD | 11 | 33 | Girlington | BRADFORD WEST | BD1 3SH | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | RAWSON SPRING ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 1PD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1408 | 3.0638 | 2.9878 | 2.6788 | 2.4538 | 2.3198 | 2.2028 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | REVILL LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S13 7QX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ROCKWARE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4RH | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | RODLEY LANE | 11 | 33 | Rodley | SKELTON GRANGE | LS13 1LJ | NZE (DFES Best View Scenario) | 0.68921 | 0.56321 | 0.42121 | 0.26921 | 0.10021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ROMAN AVENUE | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS8 2DY | NZE (DFES Best View Scenario) | 20.4416 | 20.3366 | 20.2186 | 20.0916 | 19.9496 | 19.7986 | 19.6516 | 19.5086 | 19.3666 | 19.2266 | 18.6566 | 18.2416 | 17.9936 | 17.7776 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | ROYDS LANE | 11 | 33 | Wakefield North | SKELTON GRANGE | LS26 0BE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD1 6SE | NZE (DFES Best View Scenario) | 11.8878 | 11.8468 | 11.8008 | 11.7518 | 11.6958 | 11.6368 | 11.5798 | 11.5238 | 11.4678 | 11.4128 | 11.1878 | 11.0218 | 10.9208 | 10.8328 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SAINT STREET | 11 | 33 | Girlington | BRADFORD WEST | BD7 4EH | NZE (DFES Best View Scenario) | 12.3876 | 12.3156 | 12.2346 | 12.1486 | 12.0516 | 11.9476 | 11.8476 | 11.7496 | 11.6526 | 11.5576 | 11.1666 | 10.8816 | 10.7116 | 10.5626 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SALTERFORTH | 11 | 33 | Silsden | BRADFORD WEST | BB18 6JD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SALTERHEBBLE | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX3 0QH | NZE (DFES Best View Scenario) | 19.4866 | 19.3626 | 19.2256 | 19.0766 | 18.9126 | 18.7366 | 18.5646 | 18.3946 | 18.2236 | 18.0526 | 17.3396 | 16.7996 | 16.4506 | 16.1356 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SALTSHOUSE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU8 9HR | NZE (DFES Best View Scenario) | 21.3072 | 21.2192 | 21.1212 | 21.0152 | 20.8962 | 20.7702 | 20.6482 | 20.5292 | 20.4132 | 20.2992 | 19.8392 | 19.5112 | 19.3232 | 19.1632 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SANDHILL LANE | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | YO41 4DF | NZE (DFES Best View Scenario) | 0.2827 | 0.2357 | 0.1827 | 0.1257 | 0.062702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SAXON ROAD | 11 | 33 | Norton Lees | NORTON LEES | S8 0XQ | NZE (DFES Best View Scenario) | 2.1872 | 2.0642 | 1.9262 | 1.7782 | 1.6122 | 1.4352 | 1.2642 | 1.0972 | 0.93118 | 0.76818 | 0.10218 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SCARTHO | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN33 3JL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SCHOLES | 11 | 33 | Thornhill 132kV | ELLAND | HD9 1UG | NZE (DFES Best View Scenario) | 0.84913 | 0.75813 | 0.65613 | 0.54613 | 0.42413 | 0.29413 | 0.16713 | 0.043129 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SCISSETT | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SCULCOATES A | 11 | 132 | Sculcoates A | CREYKE BECK | HU5 1DA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SEACROFT | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 1LU | NZE (DFES Best View Scenario) | 13.148 | 13.064 | 12.969 | 12.867 | 12.753 | 12.632 | 12.514 | 12.399 | 12.285 | 12.173 | 11.716 | 11.382 | 11.183 | 11.01 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SEATON | 11 | 66 | Driffield/Beverley Group | CREYKE BECK | HU11 5RQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SELBY | 11 | 33 | Osgodby 3/4 | DRAX | YO8 8NB | NZE (DFES Best View Scenario) | 0.38857 | 0.013572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SELBY ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS15 0QE | NZE (DFES Best View Scenario) | 19.8916 | 19.7516 | 19.5946 | 19.4256 | 19.2366 | 19.0356 | 18.8396 | 18.6496 | 18.4606 | 18.2746 | 17.5166 | 16.9636 | 16.6336 | 16.3466 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SHARLSTON | 11 | 33 | Featherstone | FERRYBRIDGE B | WF4 1BE | NZE (DFES Best View Scenario) | 11.9117 | 11.7407 | 11.5497 | 11.3447 | 11.1157 | 10.8707 | 10.6337 | 10.4017 | 10.1727 | 9.9457 | 9.0197 | 8.3427 | 7.9367 | 7.5817 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SHEPCOTE TINSLEY | 11 | 33 | Wincobank | WINCOBANK | S9 1RF | NZE (DFES Best View Scenario) | 30.0977 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | 30.0967 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SHERBURN | 11 | 33 | Bramham | FERRYBRIDGE B | LS25 6PL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SHIPLEY | 11 | 33 | Bradford | BRADFORD WEST | DN21 5UT | NZE (DFES Best View Scenario) | 25.8655 | 25.7765 | 25.6775 | 25.5705 | 25.4505 | 25.3235 | 25.1995 | 25.0795 | 24.9595 | 24.8415 | 24.3605 | 24.0095 | 23.7995 | 23.6165 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SHIRLAND LANE | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3GD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SILVER STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 2DU | NZE (DFES Best View Scenario) | 2.7493 | 2.7293 | 2.7073 | 2.6843 | 2.6583 | 2.6303 | 2.6033 | 2.5763 | 2.5503 | 2.5243 | 2.4193 | 2.3423 | 2.2973 | 2.2573 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SILVERWOOD | 11 | 66 | Thurcroft | THURCROFT | S65 4PR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SKILLINGS LANE | 11 | 33 | Hull West | CREYKE BECK | HU15 1EQ | NZE (DFES Best View Scenario) | 2.2874 | 2.1634 | 2.0254 | 1.8764 | 1.7134 | 1.5374 | 1.3634 | 1.1894 | 1.0104 | 0.82739 | 0.041394 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SKIPTON | 11 | 33 | Silsden | BRADFORD WEST | BD23 2RR | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SLAITHWAITE | 11 | 33 | Lindley | ELLAND | HD7 6LS | NZE (DFES Best View Scenario) | 0.72786 | 0.63686 | 0.53386 | 0.42386 | 0.30086 | 0.16986 | 0.041862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SLEDMERE GARTH | 11 | 33 | Whinmoor | FERRYBRIDGE B | LS14 5DS | NZE (DFES Best View Scenario) | 18.704 | 18.648 | 18.585 | 18.517 | 18.441 | 18.36 | 18.282 | 18.206 | 18.13 | 18.055 | 17.751 | 17.529 | 17.397 | 17.281 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SMITH STREET | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF10 2RY | NZE (DFES Best View Scenario) | 12.6639 | 12.5739 | 12.4729 | 12.3639 | 12.2429 | 12.1129 | 11.9869 | 11.8639 | 11.7419 | 11.6219 | 11.1319 | 10.7739 | 10.5589 | 10.3709 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SMITHY GREEN | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SNAITHING PARK ROAD | 11 | 33 | Norton Lees | NORTON LEES | S10 3LJ | NZE (DFES Best View Scenario) | 0.060323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SNELSINS LANE | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 3UH | NZE (DFES Best View Scenario) | 16.2996 | 16.2146 | 16.1206 | 16.0186 | 15.9056 | 15.7846 | 15.6666 | 15.5516 | 15.4376 | 15.3246 | 14.8626 | 14.5236 | 14.3176 | 14.1376 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH ELMSALL | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 2JH | NZE (DFES Best View Scenario) | 23.0724 | 22.9554 | 22.8254 | 22.6844 | 22.5284 | 22.3614 | 22.1984 | 22.0404 | 21.8834 | 21.7274 | 21.0924 | 20.6274 | 20.3474 | 20.1024 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH FERRIBY | 11 | 33 | Santon | KEADBY | DN18 6JL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH KIRKBY | 11 | 66 | Ferrybridge A | FERRYBRIDGE A | WF9 3TJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH RESTON | 11 | 33 | Wold Newton | KEADBY | LN11 8JQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SOUTH STREET | 11 | 33 | Bingley 132/33kV | BRADFORD WEST | BD21 1AH | NZE (DFES Best View Scenario) | 7.5989 | 7.4969 | 7.3829 | 7.2599 | 7.1239 | 6.9769 | 6.8359 | 6.6969 | 6.5599 | 6.4249 | 5.8739 | 5.4709 | 5.2299 | 5.0199 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHGATE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | YO43 3BE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 18.7766 | 18.6106 | 18.4446 | 18.2736 | 18.0996 | 17.3506 | 16.7586 | 16.3416 | 15.9526 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SOUTHWOOD ROAD | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU16 5AN | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | HX6 1EN | NZE (DFES Best View Scenario) | 24.0912 | 23.9502 | 23.7932 | 23.6232 | 23.4352 | 23.2342 | 23.0372 | 22.8432 | 22.6482 | 22.4532 | 21.6382 | 21.0222 | 20.6232 | 20.2642 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SPARK MILL LANE | 11 | 33 | Beverley 132/33kV | CREYKE BECK | HU17 0TT | NZE (DFES Best View Scenario) | 5.6682 | 5.3772 | 5.0522 | 4.7042 | 4.3202 | 3.9072 | 3.4972 | 3.0872 | 2.6672 | 2.2402 | 0.39421 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SPENBOROUGH | 11 | 33 | Brighouse 132/33kV | ELLAND | BD19 5BT | NZE (DFES Best View Scenario) | 16.4635 | 16.3375 | 16.1965 | 16.0445 | 15.8755 | 15.6935 | 15.5175 | 15.3465 | 15.1755 | 15.0065 | 14.3145 | 13.8055 | 13.4955 | 13.2245 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SPRING MILL STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD5 7HF | NZE (DFES Best View Scenario) | 3.4538 | 3.3988 | 3.3378 | 3.2728 | 3.1998 | 3.1208 | 3.0458 | 2.9718 | 2.8978 | 2.8258 | 2.5308 | 2.3158 | 2.1868 | 2.0738 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | STAINFORTH | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN7 5HG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | STAIRFOOT | 11 | 33 | Hunningley | WEST MELTON SECTION 3 | S71 5AD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | STANLEY STREET | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S3 8HG | NZE (DFES Best View Scenario) | 3.0873 | 3.0493 | 3.0073 | 2.9623 | 2.9123 | 2.8583 | 2.8063 | 2.7553 | 2.7053 | 2.6553 | 2.4523 | 2.3053 | 2.2163 | 2.1403 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | STANNINGTON ROAD | 11 | 33 | Neepsend | NEEPSEND | S6 5FH | NZE (DFES Best View Scenario) | 1.6476 | 1.4636 | 1.2576 | 1.0366 | 0.78963 | 0.52663 | 0.27062 | 0.020625 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | STATION ROAD | 11 | 33 | Scunthorpe North | KEADBY | DN15 6BT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | STEVENSON ROAD | 11 | 33 | Pitsmoor 3/4 | PITSMOOR 3/4 | S9 3XG | NZE (DFES Best View Scenario) | 1.1752 | 1.1752 | 1.1742 | 1.1742 | 1.1742 | 1.1742 | 1.1732 | 1.1732 | 1.1732 | 1.1722 | 1.1712 | 1.1712 | 1.1702 | 1.1702 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | STOKE STREET | 11 | 33 | Attercliffe | WEST MELTON / THORPE MARSH | S9 3QN | NZE (DFES Best View Scenario) | 0.145 | 0.144 | 0.143 | 0.142 | 0.141 | 0.139 | 0.138 | 0.137 | 0.136 | 0.134 | 0.129 | 0.126 | 0.124 | 0.122 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 132/11KV | 11 | 132 | Stourton 132/11kV | SKELTON GRANGE | LS10 1SP | NZE (DFES Best View Scenario) | 1.2711 | 1.2681 | 1.2641 | 1.2601 | 1.2561 | 1.2511 | 1.2461 | 1.2421 | 1.2371 | 1.2331 | 1.2151 | 1.2021 | 1.1941 | 1.1871 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | STOURTON 33/11KV | 11 | 33 | Low Road | SKELTON GRANGE | LS10 1AX | NZE (DFES Best View Scenario) | 5.567 | 5.514 | 5.456 | 5.393 | 5.322 | 5.247 | 5.175 | 5.104 | 5.033 | 4.964 | 4.681 | 4.475 | 4.352 | 4.245 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | STOW | 11 | 33 | Blyton | KEADBY | LN1 2AJ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SWAN BANK LANE | 11 | 33 | Halifax 132/33kV | ELLAND | HX3 9XT | NZE (DFES Best View Scenario) | 1.3343 | 1.2493 | 1.1543 | 1.0523 | 0.93935 | 0.81735 | 0.69935 | 0.58135 | 0.46335 | 0.34535 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SWEET STREET | 11 | 33 | Low Road | SKELTON GRANGE | LS11 9TZ | NZE (DFES Best View Scenario) | 7.639 | 7.624 | 7.608 | 7.59 | 7.57 | 7.549 | 7.529 | 7.509 | 7.489 | 7.47 | 7.391 | 7.333 | 7.299 | 7.269 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | SWINNOW MOOR | 11 | 33 | Rodley | SKELTON GRANGE | LS13 4RJ | NZE (DFES Best View Scenario) | 2.2665 | 2.1385 | 1.9955 | 1.8415 | 1.6705 | 1.4875 | 1.3095 | 1.1365 | 0.96447 | 0.79547 | 0.10647 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | TADCASTER | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9PA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | TANKERSLEY PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S35 2PT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S60 1AD | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | THORNBURY | 11 | 33 | Rodley | SKELTON GRANGE | BD3 7AD | NZE (DFES Best View Scenario) | 4.9373 | 4.8383 | 4.7263 | 4.6063 | 4.4723 | 4.3303 | 4.1913 | 4.0563 | 3.9223 | 3.7893 | 3.2503 | 2.8573 | 2.6213 | 2.4163 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | THORNE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN8 4NA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | THORNTON | 11 | 33 | Holmfield | BRADFORD WEST | BD13 3DP | NZE (DFES Best View Scenario) | 19.8402 | 19.6722 | 19.4842 | 19.2822 | 19.0562 | 18.8152 | 18.5802 | 18.3522 | 18.1262 | 17.9032 | 16.9932 | 16.3282 | 15.9292 | 15.5822 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | THORPE ROAD | 11 | 33 | Osgodby 3/4 | DRAX | DN14 7PA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | TICKHILL ROAD | 11 | 66 | Thurcroft | THURCROFT | S66 7QN | NZE (DFES Best View Scenario) | 28.9414 | 28.7724 | 28.5844 | 28.3814 | 28.1564 | 27.9144 | 27.6794 | 27.4504 | 27.2214 | 26.9944 | 26.0624 | 25.3734 | 24.9494 | 24.5744 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | TINGLEY | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | WF3 1SS | NZE (DFES Best View Scenario) | 0.0096147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY PARK ROAD | 11 | 33 | Wincobank | WINCOBANK | S9 5DL | NZE (DFES Best View Scenario) | 2.8527 | 2.8457 | 2.8367 | 2.8277 | 2.8177 | 2.8067 | 2.7967 | 2.7857 | 2.7757 | 2.7657 | 2.7247 | 2.6957 | 2.6777 | 2.6617 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | Blackburn Meadows B | WEST MELTON / THORPE MARSH | S9 1TY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | TIVERTON ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 4DA | NZE (DFES Best View Scenario) | 1.3801 | 1.2831 | 1.1751 | 1.0581 | 0.92814 | 0.78814 | 0.65314 | 0.52314 | 0.39514 | 0.26914 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | TODMORDEN | 11 | 33 | Sowerby Bridge 132/33kV | ELLAND | OL14 7NB | NZE (DFES Best View Scenario) | 12.74 | 12.646 | 12.541 | 12.428 | 12.303 | 12.169 | 12.037 | 11.908 | 11.778 | 11.648 | 11.104 | 10.693 | 10.427 | 10.187 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | TOLLER LANE | 11 | 33 | Girlington | BRADFORD WEST | BD9 5LE | NZE (DFES Best View Scenario) | 21.2052 | 21.1022 | 20.9872 | 20.8632 | 20.7242 | 20.5762 | 20.4332 | 20.2932 | 20.1542 | 20.0182 | 19.4602 | 19.0522 | 18.8082 | 18.5962 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | TONG STREET | 11 | 33 | Staygate | SKELTON GRANGE | BD4 9PP | NZE (DFES Best View Scenario) | 3.2222 | 3.1672 | 3.1062 | 3.0402 | 2.9662 | 2.8882 | 2.8122 | 2.7372 | 2.6642 | 2.5912 | 2.2942 | 2.0782 | 1.9482 | 1.8352 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | UPPER BASINGHALL STREET | 11 | 33 | Kirkstall C 2/5 | KIRKSTALL B | LS1 5JS | NZE (DFES Best View Scenario) | 4.33 | 4.321 | 4.311 | 4.301 | 4.289 | 4.276 | 4.264 | 4.252 | 4.24 | 4.229 | 4.181 | 4.146 | 4.126 | 4.108 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | VARLEY STREET | 11 | 33 | Rodley | SKELTON GRANGE | LS28 6AN | NZE (DFES Best View Scenario) | 22.6104 | 22.4974 | 22.3704 | 22.2334 | 22.0814 | 21.9184 | 21.7604 | 21.6064 | 21.4544 | 21.3034 | 20.6914 | 20.2444 | 19.9774 | 19.7454 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | VICTORIA STREET | 11 | 33 | Sheffield City | SHEFFIELD CITY | S1 4DP | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42142 | 0.38742 | 0.35442 | 0.21842 | 0.12042 | 0.061419 | 0.010419 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WALESBY | 11 | 33 | Wold Newton | KEADBY | LN8 3UL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WARREN LANE | 11 | 33 | Bramham | FERRYBRIDGE B | LS24 9NT | NZE (DFES Best View Scenario) | 3.8558 | 3.8248 | 3.7908 | 3.7538 | 3.7128 | 3.6688 | 3.6258 | 3.5838 | 3.5418 | 3.5008 | 3.3308 | 3.2048 | 3.1278 | 3.0598 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WATH UPON DEARNE | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S63 7DX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | Wincobank | WINCOBANK | S60 5BL | NZE (DFES Best View Scenario) | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5036 | 30.5026 | 30.5026 | 30.5026 | 30.5026 | 30.5016 | 30.5016 | 30.5016 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WAWNE ROAD | 11 | 33 | Bransholme | CREYKE BECK | HU7 5BT | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WEELAND ROAD | 11 | 33 | Kirkhaw Lane | FERRYBRIDGE B | WF11 0LA | NZE (DFES Best View Scenario) | 7.1271 | 7.0691 | 7.0041 | 31.0816 | 31.0036 | 30.9206 | 30.8396 | 30.7606 | 30.6826 | 30.6056 | 30.2896 | 30.0586 | 29.9196 | 29.7986 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WELLINGTON STREET | 11 | 33 | Featherstone | FERRYBRIDGE B | WF10 1NW | NZE (DFES Best View Scenario) | 12.8601 | 12.7621 | 12.6531 | 12.5361 | 12.4051 | 12.2641 | 12.1281 | 11.9961 | 11.8641 | 11.7351 | 11.2051 | 10.8171 | 10.5851 | 10.3811 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WESLEY CRESCENT | 11 | 33 | Humberston | GRIMSBY WEST | DN35 0JU | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WEST DOCKS | 11 | 33 | Hull South | CREYKE BECK | HU3 4UU | NZE (DFES Best View Scenario) | 1.7723 | 1.7683 | 1.7633 | 1.7583 | 1.7523 | 1.7453 | 1.7393 | 1.7333 | 1.7273 | 1.7213 | 1.6983 | 1.6823 | 1.6723 | 1.6643 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WEST END LANE | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN11 0PU | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WEST MOOR PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN3 3FE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WEST PARK | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS16 5PS | NZE (DFES Best View Scenario) | 7.0156 | 6.9256 | 6.8246 | 6.7156 | 6.5946 | 6.4646 | 6.3386 | 6.2166 | 6.0946 | 5.9746 | 5.4876 | 5.1316 | 4.9196 | 4.7346 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WESTCOTT STREET | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU8 8JN | NZE (DFES Best View Scenario) | 0.85689 | 0.69689 | 0.51789 | 0.32489 | 0.10989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WHEATACRE ROAD | 11 | 66 | Hunshelf | WEST MELTON SECTION 3 | S36 2GQ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WHEATLEY PARK | 11 | 66 | Doncaster B/Thorpe Marsh | WEST MELTON / THORPE MARSH | DN2 4PG | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WHINGATE | 11 | 33 | Kirkstall C/Ring Road Horsforth | KIRKSTALL B | LS12 3QT | NZE (DFES Best View Scenario) | 19.8291 | 19.7551 | 19.6711 | 19.5811 | 19.4811 | 19.3741 | 19.2701 | 19.1691 | 19.0691 | 18.9701 | 18.5671 | 18.2731 | 18.0971 | 17.9451 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WHITE LEE | 11 | 33 | Heckmondwike | SKELTON GRANGE | WF17 8AF | NZE (DFES Best View Scenario) | 1.8215 | 1.6655 | 1.4915 | 1.3035 | 1.0945 | 0.8705 | 0.6535 | 0.4415 | 0.2305 | 0.021502 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | Low Road | SKELTON GRANGE | LS1 4HR | NZE (DFES Best View Scenario) | 7.773 | 7.769 | 7.764 | 7.759 | 7.754 | 7.748 | 7.743 | 7.738 | 7.732 | 7.727 | 7.705 | 7.69 | 7.681 | 7.672 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | Beeston Royds 132/33kV | KIRKSTALL B | LS1 4BN | NZE (DFES Best View Scenario) | 18.6989 | 18.6919 | 18.6849 | 18.6769 | 18.6689 | 18.6599 | 18.6509 | 18.6419 | 18.6339 | 18.6249 | 18.5909 | 18.5659 | 18.5509 | 18.5379 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WIBSEY | 11 | 33 | Staygate | SKELTON GRANGE | BD6 3BG | NZE (DFES Best View Scenario) | 0.50726 | 0.36026 | 0.19526 | 0.019261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WITHERNSEA | 11 | 33 | Hull East 132/33kV | SALTEND NORTH | HU19 2QA | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WOODCOCK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 5LL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WOODSEATS | 11 | 33 | Jordanthorpe | JORDANTHORPE | S8 8QB | NZE (DFES Best View Scenario) | 2.1287 | 2.0117 | 1.8807 | 1.7407 | 1.5827 | 1.4157 | 1.2527 | 1.0937 | 0.93669 | 0.78169 | 0.14869 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WOOLLEY | 11 | 66 | Barugh 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WORSBROUGH PARK | 11 | 66 | West Melton | WEST MELTON SECTION 3 | S70 5LY | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | WRAWBY | 11 | 33 | Santon | KEADBY | DN20 8SX | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | Yarborough Road 132/33kV | GRIMSBY WEST | DN34 4BL | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | YEW GREEN ROAD | 11 | 33 | Saint Andrews Road 132/33kV | SKELTON GRANGE | HD4 5DD | NZE (DFES Best View Scenario) | 1.285 | 1.172 | 1.046 | 0.91097 | 0.75997 | 0.59897 | 0.44297 | 0.28997 | 0.13797 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | YORK ROAD | 11 | 33 | Leeds East | SKELTON GRANGE | LS9 6TF | NZE (DFES Best View Scenario) | 20.6901 | 20.5541 | 20.4021 | 20.2381 | 20.0561 | 19.8611 | 19.6721 | 19.4871 | 19.3051 | 19.1251 | 18.3911 | 17.8551 | 17.5361 | 17.2581 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)
NPgY | YORK STREET | 11 | 33 | Wakefield Monckton Road | WEST MELTON SECTION 3 | WF1 3AZ | NZE (DFES Best View Scenario) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | NPg - Early Net Zero | Network Capacity Generation Headroom (MVA)

## References & Methodology
Note 1 | Generation Thermal Headroom (MVA) | This is the MVA headroom for each scenario's future projection of generation forecasting.
It is calculated by comparing the gap between the future projected value, substation potential reverse power flow capability and upstream network constraints.
Where there are known fault level constraints the network generation headroom is defined as zero headroom available. Planned network interventions have been included in the forecast headroom predictions.
Network constraints at the GSPs have not included within this generation headroom report and further analysis would be required.
Note 2 | Using the spreadsheet | Filter on any substation to see all the scenarios for that substation.
Note 3 | The best view plan and the DFES scenarios | The best view plan (planning scenario) comes after DFES publication and is informed by analysis of the full scenario range together with other factors.
This plan aligns to the ED2 draft business plan published in July 2021.
Note 4 | The five DFES scenarios | The DFES scenarios come from DFES 2020 and include a regionalisation of the four NG FES scenarios to our network and a fifth scenario.
The fifth DFES scenario is called Net Zero Early and is our best view scenario incorporating latest national policy and regional knowledge / stakeholder feedback at the time of DFES publication.
Note 5 | References | Fuller descriptions of our methodologies for producing scenarios and producing a best view plan can be found in the scenarios appendix at the link below.
https://ed2plan.northernpowergrid.com/sites/default/files/inline-files/Scenarios_and_investment_planning.pdf
Links to our DFES 2020 product (document and data and map visualisation tool) can be found from the signposting links in the DFES document below.
https://www.northernpowergrid.com/asset/1/document/5836.pdf
The Energy Networks Association (ENA) report for proposals for the Form of Statement of Network Development Plans.
https://www.energynetworks.org/assets/images/Resource%20library/ON21-WS1B-P5%20Network%20Development%20Plan%20Form%20of%20Statement%20(19%20Aug%202021).pdf
Note 6 | Actuals (current position) | Please refer to our heatmaps for actual headroom. This report is only concerned with forecast headroom.
https://www.northernpowergrid.com/generation-availability-map
Note 7 | Contacts | npg.system.planning@northernpowergrid.com
Document Control
| Engineer | Victoria Gosling (System Planning Engineer)
| Reviewed | Simon Jesson (System Planning Manager)
| Approved | Joanne Kerrigan
| Revision | V1.0
| Published | 31st August 2021